# CHAPTER 1
# INTRODUCTION
## Motivation For the Thesis
In today’s society, energy supply is one of the main interests and energy consumption is considered as an important parameter to analyze the level of development of a society. World’s total energy consumption has been increasing throughout the years and it is expected to grow by 45% in 2040 [1]⁠.
Since the industrial revolution, fossil fuels are remained as the main source of energy. However, negative impacts of these sources led the search for alternative methods to fulfill energy requirements. Climate change, which is the result of increasing greenhouse gases in the atmosphere, is the main concern about fossil fuels. Moreover, fossil fuels are non-renewable energy sources, so there is a limited supply.
Renewable energy generation has been growing rapidly, with wind power having the highest percentage. Today, wind energy is the most popular renewable energy source with 3.7% of the global electricity supply and this percentage is expected to increase for the next years [2]⁠. At the end of 2016, total installed wind power capacity has reached to approximately 487 GW and is expected to reach around 790 GW in 2020 [3]⁠. Increase in the installed wind capacity over years globally and in Turkey can be observed in Fig. 1-1 [4]⁠ and Fig. 1-2 [5]⁠, respectively.

Fig. 1-1: Historical development of global installed wind capacity [4]⁠

Fig. 1-2: Historical development of installed wind capacity in Turkey [5]⁠
Power output of a wind turbine is highly dependent on wind speed and can be expressed as follows:
P = {1} over {2} %rho_air A v^3 C_p
where:
P	power output
%rho_air	air density
A	swept area
v	wind speed
C_p	power coefficient, function of speed ratio and pitch angle
Power output of a wind turbine is proportional to the cube of the wind speed, so even small variations of wind speed can cause large fluctuations in the power output.

Fig. 1-3: Typical output of wind turbine versus wind speed [6]⁠
Typical output of a wind turbine with changing wind speed is shown in Fig. 1-3 [6]⁠. At low speeds, enough torque cannot be exerted by the wind to rotate the turbine blades. With increasing wind speed, at some point the turbine blades will overcome friction and begin to rotate. The speed at which the turbine begins to rotate is called cut-in speed.
Above cut-in speed, power output of the wind turbine rapidly increases. The power output reaches the maximum limit of the generator in some point, which is called rated power output. After this point, increase in wind speed does not affect the power output of the wind turbine, as the design of the turbine is arranged to limit the power output.
With increasing wind speed, the forces on the turbine also increase and at some point the rotor is brought to a standstill with a breaking system in order to prevent possible damage. This critical speed is called cut-out speed.
In Fig. 1-4, daily fluctuations of power output of a wind farm in Turkey can be observed. It can be seen that the power output can have steep rises and sudden drops.

Fig. 1-4: Daily generation of a wind farm in Turkey
With the increasing penetration of wind energy to power systems, energy balance problem becomes harder to achieve, as a consequence of unpredictable and varying nature of wind. Considering expected share of wind generation in overall electric power generation to grow significantly over the years, more flexibility in power systems will be required to handle with the negative impacts of wind power. In the near future, system flexibility needs, which has been driven by variable demand up to this day, will begin to be driven by supply variability.
The impact of increasing wind power penetration level to stability and reliability of the system can be summarized as follows [7]⁠:
Reliability problems: Net-load variations can be tracked by Conventional Generators (CGs) at low level integration of wind power to the power system [8]⁠. However, increasing penetration of wind energy eventually affects the system reliability as wind generation is generally not related to the demand pattern which leads to an increase on the net-load difference between peak and off-peak periods. As a result, committed CGs cannot catch the sudden and large changes of wind power output and additional operating reserves with better dynamic performance to compensate the difference will be required to maintain system reliability.
Stability problems: Wind Turbine Generators (WTGs) can provide small or even no contributions to frequency support unlike synchronous generators [9]⁠. Wind power output fluctuations will also weaken voltage stability of the system due to generation and load mismatch [10]⁠.
For the integration of renewable energy into power system effectively, four main options are proposed for providing flexibility to the power systems: dispatchable generation, transmission and distribution expansion, demand-side management and energy storage [11]⁠.
This thesis focuses on impact of energy storage systems (ESSs) and demand-side management (DSMs) applications in a long run.
## Aims of the Research
Variability and uncertainty are important issues for power systems, and to cover the deviations from equilibrium and unexpected situations, enough energy resources are needed. However, the capacity of resources for the flexibility of given power system must be analyzed carefully as providing flexibility is rather expensive.
In this thesis, contribution of energy storage and demand side management technologies to high penetration of wind power generation is studied.
Applications of energy storage for this purpose can be summarized as follows [11]⁠:
Electricity time shift: Electric power can be stored when generation exceeds demand and stored power can be supplied to the grid when demand exceeds generation. With electricity time shift, the stability of the power system increases as the net-load is reduced.
- Conversion to other energy carriers: Electric power can be transformed into a different energy form and stored for later use in this form. Thermal energy is one example of this usage, as the heat is used for space and water heating in residential and commercial buildings.
- Provision of frequency reserve and grid services: When an unexpected excess in power generation occurs, storage capacity can be committed to charging and when an unexpected excess in power demand occurs, storage capacity can be committed to discharging. By doing so, the effects of unexpected fluctuation in the balance of supply and demand can be reduced.
- Transmission and distribution investment deferral: Storage can be used for absorbing power above the capacity of T&D line or component and releasing the stored energy when the T&D capacity is suitable. High costs of T&D upgrades can be deferred with relatively small amounts of storage.
## Outline of the Thesis

# CHAPTER 2
# PROVIDING FLEXIBILITY INTO POWER SYSTEMS FOR WIND POWER INTEGRATION
## Introduction
The main concern about planning and operation of the power systems is maintaining the equilibrium between security and efficiency. With the increasing penetration of renewable generation into power systems, sustaining this equilibrium becomes a more complicated problem to be solved. In order to reduce the impacts of renewable generation into power systems, further flexibility is required.
Flexibility of power systems is defined as the ability of a power system to respond to changes in demand and supply over a range of operating conditions [12]⁠. All power systems contain some degree of flexibility, as variability and uncertainty are always an issue and systems are designed to match the supply and demand all the time. However, with the renewable generation integration into power systems, variability and uncertainty become a problem of generation-side, in addition to load-side of the systems.
For better understanding, impact of wind generation on net-load can be observed in Fig. 2-1 [12]⁠. Here, net-load represents the demand which will be supplied by the CGs when the wind generation is utilized. It can be observed that wind generation leads to steeper ramps, deeper turn downs and shorter peaks which affects CG operations.

Fig. 2-1: Impact of wind generation on net-load [12]⁠
In conventional power systems, generators with fast start time, high ramp-up/down and low minimum up/down-times are used to provide flexibility. However, considering the impact of renewable generation on power systems, alternative methods are needed to compensate emerging effects. Energy storage systems (ESSs) and demand-side management (DSM) are two main methods that can be integrated into power systems to supply the additional flexibility.
In this chapter, general background of the thesis is presented. Main characteristics and applications of ESSs and DSM are explained and evaluated for the wind power integration.
## Energy Storage Systems (ESSs)
In a power system, energy demand must be supplied instantaneously to preserve stability and quality of the system. Stability and quality of a power system decreases as an imbalance between supply and demand occurs. In addition, scheduling of power systems with varying net-load profile decreases the overall efficiency because of the deviations from optimal generation spot.
Conventional power systems operate effectively without storage, but efficiency of the systems can be increased with the integration of ESSs. Additionally, ESSs can be used to reduce the effects of wind power integration and increase reliability and stability of the systems.
Considering the recent development and advances in energy storage technology, ESSs have become a suitable solution for the negative impacts of wind power integration. An ESS can be described in terms of the following properties [13]⁠:
Storage Capacity (kWh) is the amount of energy that can be stored by the ESS.
Power Rating (kW) is the rate of energy transfer per unit time which can be supplied or consumed by ESS.
Energy to Power Ratio is the ratio of the ESS storage capacity to its power. ESSs with higher energy to power ratio can deliver power for longer periods. Suitable applications for ESSs according to their maximum charge/discharge duration at rated power are summarized at Table 2.1 [13]⁠.
Table 2.1: ESS applications for different energy to power ratio [13]⁠
Energy to power ratio	seconds to minutes	daily	weekly to monthly
Applications	Primary/Secondary frequency control / Spinning reserve / Voltage control / Black start capability / Peak shaving / Island grids / Electromobility (Hybrid electric vehicle) / Uninterruptible power supply	Tertiary frequency control / Standing reserve / Load leveling / Island grids / Electromobility (Full electric vehicle) / Residential storage systems / Uninterruptible power supply	Storage for “Dark calm” periods / Island grids

Energy density is the ratio of the ESS storage capacity to its volume. ESSs with higher energy density can be used for applications where the volume of storage system is limited.
Power density is the ratio of the ESS power to its volume. ESSs with high power density can be used for high power applications with short duration of power usage.
Specific energy is the ratio of the ESS energy capacity to its weight. ESSs with high specific energy can be used for application with high energy demand and weight limitations.
Specific power is the ratio of the ESS power to its weight. ESSs with high specific power can be used for applications with high power demand and weight limitations.
Depth of Discharge (DoD) is the ratio of the amount of discharged energy to the energy capacity of ESS. DoD limitations are used for several ESS technologies, as full discharge of ESSs are not allowed for technical reasons.
State of Charge (SoC) is the ratio of the amount of remaining energy to the usable energy capacity of ESS.
Efficiency is the ratio of output energy to input energy of ESS. With increasing losses, efficiency of the ESSs decreases.
Self discharge is the energy loss of ESS due to internal processes at standby.
Start-up time is the time period between power request and first power delivery.
Ramp-up time is the time period required from zero to full power transition.
Ramp rate is the ratio of maximum power to ramp-up time.
Deployment/response time is the time period between power request and full power delivery. In Fig. 2-2 [13]⁠, time parameters of a storage system can be observed.

Fig. 2-2: Response time of a storage system [13]⁠
Full cycle is the complete discharging and charging process of ESS.
Equivalent full cycle is the overall energy throughput with any DoD per cycle divided by available capacity.
Cycle life is the number of full cycles that can be delivered by ESS under specified conditions before ESS cannot meet specified criteria.
Calendar life is the lifetime of ESS when it is not used.
While choosing the suitable ESS for a given power system, these given properties must be carefully analyzed. Storage capacity and power rating are two important parameters for these systems. Capacity rate can be determined by control and energy management procedures while power rate can be determined by the difference between supply and demand.
## Classification of ESS
A widely-used classification of energy storage technologies is according to the form of energy used [14]⁠:
- Mechanical:
  - Pumped hydro storage (PHS)
  - Compressed air energy storage (CAES)
  - Flywheel energy storage (FES)
- Electrochemical:
  - Secondary batteries
  - Flow batteries
- Chemical:
  - Hydrogen storage
  - Natural gas storage
- Electrical:
  - Super capacitor
  - Superconducting magnetic energy storage (SMES)
- Thermal:
  - Sensible heat storage
  - Phase change materials (PCM)
ESSs can be also categorized according to duration and frequency of the power supply [13]⁠:
Short-term ESS
Short-term ESSs are used for instant energy supply. This type of ESSs are used mainly in primary and secondary frequency control and reactive power compensation applications. This storage systems have low energy to power ratio of minutes and high charging and discharging rates. Generally, charging/discharging cycles per day are very high for this systems.
Medium-term ESS
Medium-term ESSs are used for matching the demand fluctuations between day and night. Energy to power ratio of this systems are between 1 to 10 hours. This type of systems have typically one or two cycles per day.
Long-term ESS
Long-term ESSs are used for power supply during several days or weeks. These systems have very high energy to power ratio, and due to this high energy capacity and relatively low power, the number of full cycles per year is very few.
Common applications of ESSs and their requirements for these applications are summarized at Table 2.2 [15]⁠. A more detailed classification of ESS applications with descriptions is also listed at Table 2.3 [16]⁠.
Table 2.2: Applications of storage systems and their requirements [15]⁠
Application type	Example of application	Power rating	Response Time	Discharge Time
Long duration, / Frequent	Bulk energy storage, / Energy arbitrage	>10 MW	minutes	4-8 hours
Medium duration, / Fast response	Capacity credit, / Spinning reserve, / T&D support	1-10 MW	seconds to minutes	0.5-2 hours
Short duration, / Highly frequent	Frequency regulation, / RES integration, / Power quality	0.1-2 MW	milliseconds to seconds	<0.25 hours

Table 2.3: Definition of ESS applications [16]⁠
	Application	Description
Generation and System Level Applications	Wholesale Energy Services	Utility-scale storage systems for bidding into energy, capacity and ancillary services markets
	Renewable Integration	Utility-scale storage providing renewables time shifting, load and ancillary services for grid integration
	Stationary Storage for T&D Support	Systems for T&D system support, improving T&D system utilization factor, and T&D capital deferral
Transmission and Distribution System Applications	Transportable Storage for T&D Support	Transportable storage systems for T&D system support and T&D deferral at multiple sites as needed
	Distributed Energy Storage Systems	Centrally managed modular systems providing increased customer reliability, grid T&D support and potentially ancillary services
	Energy Services Company Aggregated Systems	Residential-customer-sited storage aggregated and centrally managed to provide distribution system benefits
	Commercial and Industrial Power Quality and Reliability	Systems to provide power quality and reliability to commercial and industrial customers

## ESS Applications for Wind Integration Support
ESS applications for wind integration support can be categorized according to different stakeholders [7]⁠:
Generation-side Applications
Different from conventional power plants, wind farm power output cannot be controlled in a strict way as a result of stochastic nature of wind. Power intermittency, ramp rates and limiting wind power output are the main challenges coming along with wind power integration to the power systems [17]⁠. Looking from the generation-side to overall system, controllability of a wind farm can be increased with the usage of ESS.
  - Time shifting:
Wind power generation is a non-dispatchable source of electricity production and can only be forecasted with a limited certainty. The mismatch between wind power output with the demand pattern, e.g. high wind power generation during off-peak demand and vise versa, is a big challenge as the difference between the peak and off-peak periods of system net-load increases.
Energy storage technologies can be used to match the wind power generation with load cycles by storing extra energy during high wind power generation and releasing it later during peak demand periods.
In time shifting applications, huge amount of energy is required to be stored for long time periods, so it is important to consider energy capacity and energy to power ratio parameters of an ESS in these applications.
  - Output smoothing:
Wind power generation can have sudden drops and steep rises as a result of changing wind speed. System stability will be affected with the sudden power output changes which will create frequency and voltage fluctuations.
Power output of a wind farm can be smoothed out with energy storage technology applications, excess energy can be stored during instantaneous increase in power generation and released when output power drops suddenly.
Ramping capability of ESS is the most important parameter in these applications, as storage system must response the sudden changes at wind power output.
  - Transmission utilization efficiency:
Wind resources are often located in remote locations and transmission networks limitations becomes a serious problem to supply the energy demand, which is far from wind farm sites [18]⁠.
With the usage of energy storage technology, efficiency of transmission utilization can be increased by reducing congestion over the network. Additionally, transmission and distribution upgrades can be deferred or in some cases avoided at all with proper usage of ESS.
Grid-side Applications
Increasing wind power generation reduces the stability and reliability of the grid, because of the intermittent nature of these supplies. Considering the distributed generation of wind farms over the system, net variability of the entire grid is lower compared to the integration of single wind power plant, so overall requirement of services is less than considering grid-side applications.
Energy storage technology can be used to provide ancillary services to decrease the impact of wind power generation over system stability and reliability. Grid-side applications of ESS is listed according to response time of the systems at Table 2.4 [7]⁠.
Table 2.4 Grid-side applications of ESS [7]⁠
Application	Response time	Example
Energy arbitrage, / Load leveling	Hours to days	PHS, NaS, CAES, VRB
Frequency regulation	Seconds to minutes	Li-ion, NaS, FES, VRB
Inertia emulation, / Oscillation damping, / Voltage support, / LVRT	Less than a second	LA, NaS, FES, VRB
Reserves	Minutes to hours	PHS, FES, BESS
Efficiency use of transmission network	Minutes to hours	Li-ion
Emergency power supplying / Black start	Minutes to hours	LA

  - Energy arbitrage/load leveling
In the electricity market, electricity price varies during peak and off-peak hours. Hourly variation of prices in Turkey can be observed in Fig. 2-3 [19]⁠, as an average of hourly prices in 2016.
By storing low-cost energy during off-peak periods and releasing stored energy during peak periods with the higher price can reduce the gap between the peak and off-peak prices [20]⁠.

Fig. 2-3 Average of hourly electricity prices in Turkey [19]⁠
  - Frequency regulation
ESS can be used to provide frequency regulation to the wind farms by controlling active power output of storage with frequency deviation. Primary frequency control can be applied by using droop control in local systems. Active power output of ESS can be controlled according to frequency change on the grid [21]⁠. For secondary frequency control, an automatic control system can arrange the power outputs to response frequency deviations.
  - Inertia emulation
Frequency changes in a power system can be reduced by increasing the grid inertia [9]⁠. The impact of sudden wind generation changes by increasing inertia of grid which can be done by controlling the active power output of ESS.
  - Oscillation damping
Sudden power changes of wind farms can cause oscillations in an interconnected system which may led to synchronization loss of some machines [22]⁠. To damp the system oscillations caused by variable wind generation ouput, ESS can be installed to the system and so, system stability can be increased.
  - Voltage control support
Voltage stability of the grid can decrease with the variable nature of wind generation output. ESS integration can increase reactive power support for voltage regulation by controlling full scale converter connected to the grid [22]⁠.
  - Low Voltage Ride Through (LVRT) support
Today, LVRT capability of wind turbine generators (WTGs) are determined by grid codes. During severe grid faults, wind turbines should remain connected for reactive power support and in some situations maximum reactive power needs to be delivered by wind turbines. For such cases, ESS can support the power need by converters and control systems.
  - Reserve application
For the stability and reliability of the system, emergency reserves are required as a result of forecast error of wind power output. Integration of ESS can be an option for the reserve applications.
  - Emergency power supply
In the situation of a fatal failure, ESS can be used to energize the power system from a shut-down condition [23]⁠.
  - Transmission utilization efficiency
ESS integration can increase the efficiency of transmission network usage and transmission and distribution costs can be reduced by deferral of network upgrade.
Demand-side Applications
Variable loads can be used as a Virtual Power Plant (VPP) considering huge amounts. With the combination of ESS and demand side management, ancillary services can be provided using VPP.
## ESS Planning for Wind Power Integration Applications
Technical requirements of the ESS, such as power and energy capacity and charging/discharging duration range can be determined by analyzing characteristics of a wind farm.
Fluctuations of wind generation output at different time scales is an important parameter for ESS selection. Generation reserve and energy dispatch of the system is related to low frequency fluctuations (minutes to hours). On the other hand, power system frequency control is affected with high frequency fluctuations (seconds to minutes) [24]⁠.
High frequency fluctuations on the wind power output has an insignificant effect overall [25]⁠ and can be damped out by inertia of the turbine generator [26]⁠. As a result, it is required that ESS can be charged/discharged at full power capacity in hours for wind integration support [7]⁠.
Considering increasing rating capacity of wind farms, large-scale energy storage technologies are required for wind integration applications. As can be seen in Fig. 2-4 [27]⁠, BESS, PHS and CAES technologies are suitable for these applications, which can store energy for long periods at a high power rating. Among these three technologies, BESS is more suitable for the purpose, as PHS and CAES are limited by topographical constraints [28]⁠.

Fig. 2-4: Comparison of storage technologies [27]⁠
By taking account of the findings mentioned above and rapid development in battery technology and cost reduction, it is decided to study the BESS technology for the wind power applications.
Energy capacity and power ratings are the main parameters to be determined for the wind power applications of storage systems. ESS size determination can be modeled as an optimization problem considering application purpose, control strategy and economical aspects [7]⁠.
Two mainly used battery types in BESSs are lithium-ion and lead-acid batteries and their characteristics are summarized including future expectations, at Table 2.5 and Table 2.6 [13]⁠ respectively.
BESS technology is chosen for the applications in this study.
Table 2.5: Characteristics of lithium-ion batteries [13]⁠
Lithium-ion batteries
Parameters	2013	2030
Round-trip efficiency	83-86 %	85-92 %
Energy density	200-350 Wh/l	250-550 Wh/l
Power density	100-3500 W/l	100-5000 W/l
Cycle life	1000-5000 full cycles	3000-10000 full cycles
Calender life	5-20 years (depending on temperature and SoC)	10-30 years (depending on temperature and SoC)
Depth of discharge	Up to 100 %	Up to 100 %
Self discharge	5 % per month	1 % per month
Power installation cost (converter)	150-200 €/kW	35-65 €/kW
Energy installation cost	300-800 €/kW	150-300 €/kW
Deployment time	3-5 ms
Site requirements	None
Main applications	Frequency control, Voltage control, Peak shaving, Load leveling, Electromobility, Residential storage systems

Table 2.6: Characteristics of lead-acid batteries [13]⁠
Lead-acid batteries
Parameters	2013	2030
Round-trip efficiency	75-80 %	78-85 %
Energy density	50-100 Wh/l	50-130 Wh/l
Power density	10-500 W/l	10-1000 W/l
Cycle life	500-2000 full cycles	1500-5000 full cycles
Calendar life	5-15 years (depending on temperature and SoC)	10-20 years (depending on temperature and SoC)
Depth of discharge	70 %	80 %
Self discharge	0.1-0.4 % per day	0.05-0.2 % per day
Power installation cost (converter)	150-200 €/kW	35-65 €/kW
Energy installation cost	100-250 €/kW	50-80 €/kW
Deployment time	3-5 ms
Site requirements	Ventilation due to gassing
Main applications	Frequency control, Peak shaving, Load leveling, Island grids, Residential storage systems, Uninterruptible power supply

## Demand-side Management (DSM)
## In a conventional power system, the balance between generation and demand is maintained by controlling a limited number of power plants. However, with the increasing penetration of renewable generation to the system, dispatch of generation capacity to provide the required services to follow the load profile becoming much more difficult.
## As an alternative way, controlling load-side to increase flexibility of the power system attracts increasing attention. With the help of global communication infrastructure and embedded systems, loads can be dispatched according to system needs [29]⁠.
With demand-side management (DSM), flexible loads can be scheduled considering the grid needs. If individual loads can be aggregated and controlled on command according to needs of power systems, the result will be the same as generation dispatch. For example, turning off a large number of loads when the demand exceeds generation will affect the system as if the generation is increased and vice versa.
## Classification of DSM
DSM is defined as all the applications which can be applied to the demand-side of the power system. DSM can be categorized according to timing and impact of the applications, which can be observed in Fig. 2-5 [29]⁠.

Fig. 2-5: Categories of DSM [29]⁠
Energy Efficiency (EE)
EE applications include increasing the efficiency of appliances and improvements on the system properties. Changing a refrigerator with a more efficient one or applying thermal insulation to a building are some examples that can be considered as EE applications. In addition, behavioral changes of users to increase efficiency of energy usage can be included in these applications.
Time of Use (TOU)
In time of use tariffs, electricity prices change according to power consumption at that time. At peak power consumption periods (17:00-22:00 for Turkey), electricity prices are much higher compared to the rest of the day. So, customers arrange their power consumption to reduce the overall cost.
Demand Response (DR)
DR is defined as controlling flexible loads to shift power consumption from peak periods to off-peak periods. By doing so, energy consumption is not decreased but only shifted through time. However, by shifting peak power consumption through time, the overall efficiency of power system is increased. Impact of DR applications can be seen in [30]⁠.

Fig. 2-6: Impact of DR application [30]⁠
Spinning Reserve (SR)
Aggregated loads can be used for frequency regulation applications both for primary and secondary control. Primary frequency control is done by controlling active power considering frequency changes over time. In secondary frequency control, frequency is restored with additional active power to the system. With SR applications, combination of large number of loads can be controlled like a virtual power plant with negative power output to the grid.
## Applications of DSM
DSM applications can be classified according to the time scale of the load control [31]⁠:
Hours
Dispatchable loads can be controlled to match highly varying wind generation profile for a wind farm or even for a region, depending on the limits of aggregated loads. Rapid changes in wind power generation can be followed by DSM control, as the flexible loads generally have a fast response. With the usage of DSM into the power systems, the required fast-response generation capacity will be reduced.
Seconds to minute
The ancillary services for power system regulation is provided by power plants in today’s power systems. An alternative way for serving these services to the power system is DSM. By controlling high number of loads with fast response, regulation can be provided in an efficient way.
Under a second
Frequency changes in a system can be observed and dispatchable loads can respond to these changes to maintain system security. Either loads can be shut down when a steep frequency drop occurs on the grid, or they can response to frequency changes according to frequency error, similar like droop control of conventional power plants. As wind power plants cannot participate to droop control, demand dispatch can be a solution for the intermittent wind power output.
## DSM Planning for Wind Power Integration Applications
DSM takes advantage of controllable loads and support the grid considering changing needs, so in order to dispatch loads, some flexibility is needed in demand-side. Flexible loads can be categorized by their impact to the end-user [31]⁠:
- Controlling some loads can affect the comfort of end-user, e.g. lights, air conditioning.
- Some loads can be controlled and affect end-user slightly or not at all, e.g. charging a plug-in vehicle at night.
Some suitable loads for DSM applications can be listed as follows [31]⁠:
- dishwashers
- washers and dryers
- electric hot water heaters
- Heating, ventilation and air-conditioning (HVAC) systems
- battery charges for consumer electronics
- plug-in vehicles
Considering the large number of aggregated flexible loads, demand dispatch can be an important factor for the power systems applications. However, there are some constraints for the flexible loads such as minimum and maximum power limits which they can draw from the grid and maximum energy drawing capacity.
Some important parameters must be defined for each individual load, such as minimum and maximum power limits, how much and when energy is needed and number of cycles for a given time period. The main objective of demand dispatch is to serve the grid needs by dispatching loads while considering these limitations. Suitable services for the power systems can be developed by considering power and energy limitations of flexible loads as well as their response characteristics.
HVAC systems are chosen to be controlled in simulations in this study, as they are responsible for a high percentage of energy usage in residential, commercial and industrial sectors [32]⁠. End-use energy consumption for residential and commercial sectors can be observe in Fig. 2-7 [33]⁠.

Fig. 2-7: End-use energy consumption for residential and commercial sectors [33]⁠
Thermal behavior of a HVAC unit can be seen in Fig. 2-8 [34]⁠. With suitable control methods, HVAC systems, when aggregated, can participate in matching generation and load, as well as ancillary services to support grid.

Fig. 2-8: Thermal behavior of a HVAC unit [34]⁠
A HVAC can be described in terms of the following properties [35]⁠:
Coefficient of Performance (CoP) is the HVAC efficiency measured in cooling/heating output divided by electrical power input.
Energy Efficiency Ratio (EER) is the ratio of cooling/heating capacity of HVAC to electrical power input at full-load conditions.
Two control methods can be used for DSM applications of HVAC systems: indirect load control and direct load control; indirect load control and direct load control [34]⁠.
Indirect load control: Customers (manually) or appliances (automatically) control the loads according to the specific requirements, e.g. frequency deviation in power systems.
Direct load control: Loads are controlled directly by an operator, without considering end-user priorities.
As mentioned in [34]⁠, direct load control is more controllable and observable compared to indirect control. Considering this, direct load control is applied for controlling HVACs in this study.
## Conclusion
# CHAPTER 3
# MODELING AND APPROACHES
## In this study, Linear Programming (LP) method is chosen to solve the optimization problems. LP problem is described as optimizing the value of a linear objective function of a vector decision variables, considering the variables can only take the values defined by a set of linear constraints. As it can be observed from the previous statement, objective function and constraints of LP are linear.
Formulation of LP can be expressed as follows:
OPT z = c^T x
s.t. A x <= b
x >= 0
where:
x	decision variable vector
c	corresponding cost vector
A	linear coefficient matrix
b	linear coefficient vector
In the formulation, OPT is used to express that the cost function can be maximization/minimization, depending on the definition of the problem.
## Wind Power
All wind power generation data are obtained from Monitoring and Forecasting System Development for Wind Generated Electrical Power in Turkey (RİTM) Project of TUBITAK MAM Energy Institute. Obtained data are analyzed and organized with R programming.
## Cost Function
Cost function of this study can be written as:
MIN annual(CAPEX(BESS) + OPEX(BESS))
The different components of the cost function are given as:
annual(CAPEX(BESS)) = sum from{i=1} to {N_b} {{Stg_i * S_i^cap} over { L_i }}
annual(OPEX(BESS)) = sum from{t=1} to {T} sum from{i=1} to {N_b} ( Chg_i * (P_ch) _i^t + Dschg_i * (P_dsch) _i^t) * { {%DELTA T} over 60 }
where:
N_b	number of BESSs
T	time instances in one year period
Stg_i	capital cost of BESSi ($/MWh)
S_i^cap	storage capacity of BESSi (MWh)
L_i	life expectancy of BESSi (years)
Chg_i	charging cost of BESSi ($/MWh)
Dschg_i	discharging cost of BESSi ($/MWh)
(P_ch)_i^t	power supplied to the BESSi at time t (MW)
(P_dsch)_i^t	power drawn from the BESSi at time t (MW)
%DELTA T	time period (minutes)
## Constraints
## Power Flow Constraints
For T&D upgrade deferral application, power over the transmission line must be kept in line capacity limits. Considering the limitations, power flow constraints can be expressed as:
-P_line^max <= sum from{i=1} to {N} {[(P_wg)_i^t - (P_d)_i^t + ((P_dsch)_i^t * { %eta_dsch} - (P_ch)_i^t * {1 over %eta_ch})]} <= P_line^max
where:
P_line^max	maximum transmission line capacity (MW)
(P_wg)_i^t	wind power generation from Wi at time t (MW)
(P_d)_i^t	load power from OIZi at time t (MW)
(P_ch)_i^t	power supplied to BESSi at time t
(P_dsch)_i^t	power drawn from BESSi at time t
%eta_ch	charging efficiency of BESSi
%eta_dsch	discharging efficiency of BESSi
## BESS Constraints
## Operation Mode Constraints
BESS can operate in three modes; charging, discharging and idle. In charging mode, batteries are charged with the power drawn from grid and BESS can be considered as a load. In discharging mode, batteries are discharged and deliver power to the grid and BESS can be considered as a generation unit. In idle mode, batteries are neither charged nor discharged.
Table 3.1: Mode variables of BESS
Variable	Idle mode	Charging mode	Discharging mode
(uch)it	0	1	0
(udsch)it	0	0	1

Mode variables of BESS are tabulated at Table 3.1. Mode of the BESS can be stated as:
(u_ch)_i^t + (u_dsch)_i^t <= 1
where:
(u_ch)_i^t	charging mode indicator of BESSi at time t
(u_dsch)_i^t	discharging mode indicator of BESSi at time t
Energy Constraints
Charging efficiency of a BESS is defined as the ratio of rate of change in stored energy in BESS to power drawn from grid. Discharging efficiency of a BESS is defined as the ratio of power supplied to grid to rate of change in stored energy in BESS.
SoC of a battery is defined as available capacity of the battery expressed as a percentage of its rated capacity. SOC is an indication of how longer a battery can continue to perform before recharging is needed [36]. Depleting or overcharging a battery is not desired, so proper limitations (i.e., 30%-100%) should be defined for SoC of the battery.
Considering above definitions, energy constraints of a BESS can be expressed as:
SoC_i^t = SoC_i^{t-1} + [ (P_ch)_i^t - (P_dsch)_i^t ] * {{%DELTA T} over {60}} over { S_i^cap }
S_i^cap = E2P_i * (P_rated)_i^max
SoC_i^min <= SoC_i^t <= SoC_i^max
where:
(P_ch)_i^t	power supplied to the BESSi at time t (MW)
(P_dsch)_i^t	power drawn from BESSi at time t (MW)
(P_rated)_i^max	power rating of BESSi (MW)
S_i^cap	storage capacity of BESSi (MWh)
E2P_i	energy to power ratio of BESSi (hours)
SoC_i^t	state of charge of BESSi at time t
SoC_i^min	minimum allowed state of charge for BESSi
SoC_i^max	maximum allowed state of charge for BESSi
%DELTA T	time period (minutes)
Power Constraints
Battery charging and discharging speeds are limited by the physical and chemical characteristics of the BESS. With increasing depth of discharge (DoD), cycle life of a battery decreases and deep discharge can cause permanent damage over battery cells. To protect the battery from a permanent damage and increase the battery cycle life, proper limitation should be set for maximum discharge rating of the battery [37].
Considering above limitations, power constraints of a BESS can be expressed as:
0 <= (P_ch)_i^t <= (P_rated)_i^max * (u_ch)_i^t
0 <= (P_dsch)_i^t <= (P_rated)_i^max * (u_dsch)_i^t
where:
(P_rated)_i^max	power rating of BESSi (MW)
(P_ch)_i^t	power supplied to the BESSi at time t (MW)
(P_dsch)_i^max	discharging power rating of BESSi (MW)
(u_ch)_i^t	charging mode indicator of BESSi at time t
(u_dsch)_i^t	discharging mode indicator of BESSi at time t
## HVAC Constraints
Operation Mode Constraints
HVAC can operate in three modes; cooling, heating and idle.
Table 3.2: Mode variables of HVAC
Variable	Idle mode	Cooling mode	Heating mode
(ucl)it	0	1	0
(uht)it	0	0	1

Mode variables of HVAC are tabulated at Table 3.2. Mode of the HVAC can be stated as:
(u_cl)_i^t + (u_ht)_i^t <= 1
where:
(u_cl)_i^t	cooling mode indicator of HVACi at time t
(u_ht)_i^t	heating mode indicator of HVACi at time t
Power Constraints
In cooling mode, HVAC draws power from the grid to extract heat from the room. CoP for cooling mode is defined as the ratio of the removed heat to electrical input power. In heating mode, HVAC draws power from the grid to release heat to the room. CoP for heating mode is defined as the ratio of the delivered heat to electrical input power.
Considering these definitions, power constraints can be expressed as:
P_i^t = (CoP_cl)_i * (Q_cl)_i^t * (u_cl)_i^t + (CoP_ht)_i * (Q_ht)_i^t * (u_ht)_i^t
P_i^t	power drawn from grid at time t (kW)
(CoP_cl)_i	coefficient of performance of HVACi for cooling
(CoP_ht)_i	coefficient of performance of HVACi for heating
(Q_cl)_i^t	equivalent cooling rate of HVACi at time t (kW)
(Q_ht)_i^t	equivalent heating rate of HVACi at time t (kW)
(u_cl)_i^t	cooling mode indicator of HVACi at time t
(u_ht)_i^t	heating mode indicator of HVACi at time t
Temperature Constraints
For modeling the HVAC unit, a simplified model for temperature dynamics of a space can be created using a resistance-capacitance (RC) circuit analogy [38]⁠. The simplified thermal mass model can be used for energy conversion problems, considering entire building and average temperature of all building spaces.
In order to use HVACs for demand-side management, required flexibility is obtained by defining the minimum and maximum temperature limits of building temperatures.
Considering these definitions, temperature constraints can be expressed as:
(T_room)_i^t = (T_room)_i^{t-1} + ({(T_out)_i^{t-1} - (T_room)_i^{t-1}} over {R_i * C_i} + {(Q_ht)_i^t - (Q_cl)_i^t} over {C_i}) %DELTA t
(T_room)_i^min < (T_room)_i^t < (T_room)_i^max
where:
R_i	equivalent thermal resistance of buildingi (Co/kW)
C_i	equivalent heat capacity of buildingi (kJ/Co)
(Q_ht)_i^t	equivalent heating rate of HVACi at time t (kW)
(Q_cl)_i^t	equivalent cooling rate of HVACi at time t (kW)
(T_room)_i^t	temperature of buildingi at time t (Co)
(T_out)_i^t	temperature of ambienti at time t (Co)
(T_room)_i^min	minimum allowed temperature of buildingi (Co)
(T_room)_i^max	maximum allowed temperature of buildingi (Co)

# CHAPTER 4
# SIMULATIONS AND RESULTS
## Introduction
In this chapter, impact of BESS and demand-side management of HVAC systems on transmission-side upgrade deferral is studied.
Actual power generation data from wind farms and load data from organized industrial zones are used in simulations. R programming language is used for data analysis and missing data interpretation. It is assumed that wind power generation and load are forecasted without any error.
## BESS Cost Assumptions
CAPEX and OPEX of BESS is taken as $500/kWh and $0.2/MWh respectively [39]⁠.
## T&D Cost Assumptions
CAPEX of the T&D equipment that may be deferred for installation or replacement can be estimated from inventory analysis, system planning models and construction cost estimates. Each application is unique and dependent on the various effects, such as installation requirements and location [40]⁠. In this study, CAPEX for transmission-side upgrade is taken as $50000/km*MW.
T&D upgrade factor is defined as the amount of carrying capacity to be added to the T&D system as part of the upgrade [41]⁠. Typical upgrade factor values range from 0.25 (%25 capacity addition) to 0.50. For this study, upgrade factor is defined as 0.33.
In order to estimate the annual cost of utility capital equipment based on the total installed cost of the equipment, fixed charge rate is used. In this study, fixed charge rate is taken as 0.11 [41]⁠.
## Case 1
## Without BESS
It is assumed that wind farm is connected to near organized industrial zone through distribution line. Connection of overall system to the grid is shown in Fig. 4-1. Transmission line capacity is determined by Pgrid, which is the net-load (difference between wind generation and industrial load) of the system.

Fig. 4-1:

Grid

Pwind

Pgrid
Pload

Organized Industrial Zone
Wind Farm

In Fig. 4-2, wind generation (Pwind) and organize industrial load (Pload) over year 0 can be observed. Net-load on the transmission-side is given in Fig. 4-3 and histogram of net-load is given in Fig. 4-4. Summary of net-load over year 0 is tabulated at Table 4.1.

Fig. 4-2: Wind generation and industrial load (year 0)

Fig. 4-3: Power flow on transmission-side (year 0)

Fig. 4-4: Histogram of power flow on transmission-side
Table 4.1: Summary of net-load
minimum	1st quarter	median	mean	3rd quarter	maximum
-25.93	-11.43	-4	-0.97	8.71	34.08

Transmission-side capacity for this system is chosen as 36 MW. Maximum net-load in the current year is 34.08 MW, 5.33% below the transmission-side capacity.
For this case, 10% wind generation capacity installation to the wind farm is considered. Additionally, industrial demand growth rate are determined as 2% per year. Considering this assumptions, net-load is expected to exceed the existing transmission-side capacity by 1.8 MW, or %5 next year.
In order to avoid equipment overloading, transmission-side capacity is planned to be upgraded with 0.33 upgrade factor, from 36 MW to 48 MW. With the estimated cost of $50000/km*MW and fixed charge rate of 0.11, annual cost of the upgrade is found as $1650000.

Fig. 4-5: Transmission-side upgrade due to overloading
## With BESS
For transmission-side upgrade deferral, BESS integration to the wind farm at the common coupling point is considered, which is shown in Fig. 4-6.

Fig. 4-6:

Grid

Pwind

Pgrid
Pload

Organized Industrial Zone

Wind Farm

BESS

Pbess

For this case, BESS power rating are for suitable application is calculated as 3.6 MW. Energy to power ratio of the BESS is defined as 2, so storage capacity of the BESS is 7.2 MWh. respectively. Initial state of charge (SoC) of the BESS is defined as 1 (fully charged) and limited between 0.3 and 0.9.
Net-load on the transmission-side with the BESS integration to the wind farm can be observed in Fig. 4-7. Power output and SoC of the BESS are also shown in Fig. 4-8 and Fig. 4-9, respectively.

Fig. 4-7 Power flow on transmission-side with BESS (year 1)

Fig. 4-8: Power output of BESS (year 1)

Fig. 4-9: SoC of BESS (year 1)

# CHAPTER 5
# CONCLUSIONS AND FUTURE WORK

REFERENCES
[1]	U.S. Energy Information Administration, International Energy Outlook 2016, vol. 0484(2016), no. May 2016. 2016.
[2]	“WIND IN NUMBERS | GWEC.” [Online]. Available: http://www.gwec.net/global-figures/wind-in-numbers/. [Accessed: 11-May-2017].
[3]	“Cumulative-Market-Forecast-by-Region-2016-2020-1.jpg (2091×1123).” [Online]. Available: http://www.gwec.net/wp-content/uploads/2016/04/Cumulative-Market-Forecast-by-Region-2016-2020-1.jpg. [Accessed: 11-May-2017].
[4]	“Global-Cumulative-Installed-Wind-Capacity-2001-2016.jpg (2092×739).” [Online]. Available: http://www.gwec.net/wp-content/uploads/2012/06/Global-Cumulative-Installed-Wind-Capacity-2001-2016.jpg. [Accessed: 23-May-2017].
[5]	Turkish Wind Energy Association, “Türkiye Rüzgar Enerjisi İstatistik Raporu,” 2017.
[6]	A. Ipakchi and F. Albuyeh, “Grid of the future,” IEEE Power Energy Mag., vol. 7, no. 2, pp. 52–62, 2009.
[7]	H. Zhao, Q. Wu, S. Hu, H. Xu, and C. N. Rasmussen, “Review of energy storage system for wind power integration support,” Appl. Energy, vol. 137, pp. 545–553, 2015.
[8]	K. Dvijotham, S. Backhaus, and M. Chertkov, “Operations-Based Planning for Placement and Sizing of Energy Storage in a Grid With a High Penetration of Renewables,” vol. 98195, 2011.
[9]	Y. Sun, Z. Zhang, G. Li, and J. Lin, “Review on frequency control of power systems with wind power penetration,” Power Syst. Technol. ( …, pp. 1–8, 2010.
[10]	H. T. Le, S. Santoso, and T. Q. Nguyen, “Augmenting wind power penetration and grid voltage stability limits using ESS: Application design, sizing, and a case study,” IEEE Trans. Power Syst., vol. 27, no. 1, pp. 161–171, 2012.
[11]	“Commercialisation of Energy Storage in Europe,” no. March, p. 96, 2015.
[12]	J. Cochran et al., “Flexibility in 21st Century Power Systems,” 21st Century Power Partnersh., vol. May, p. 14, 2014.
[13]	G. Fuchs, B. Lunz, M. Leuthold, and D. U. Sauer, “Technology Overview on Electricity Storage,” Inst. Power Electron. Electr. Drives (ISEA), RWTH Aachen Univ., no. June, p. 66, 2012.
[14]	K. Han and T. Carson, “Executive summary,” Management, vol. II, pp. 10–16, 2008.
[15]	B. Zakeri and S. Syri, “Electrical energy storage systems: A comparative life cycle cost analysis,” Renew. Sustain. Energy Rev., vol. 42, pp. 569–596, 2015.
[16]	EPRI, “Electric Energy Storage Technology Options: A White Paper Primer on Applications, Costs and Benefits,” Epri, pp. 1–170, 2010.
[17]	S. Teleke, M. E. Baran, S. Member, S. Bhattacharya, and A. Q. Huang, “Optimal Control of Battery Energy Storage for Wind Farm Dispatching,” IEEE Trans. Energy Convers., vol. 25, no. 3, pp. 787–794, 2010.
[18]	“Advantages and Challenges of Wind Energy | Department of Energy.” [Online]. Available: https://energy.gov/eere/wind/advantages-and-challenges-wind-energy. [Accessed: 08-Jun-2017].
[19]	“ELEKTRİK PİYASASI,” 2016.
[20]	G. Celli, S. Mocci, F. Pilo, and M. Loddo, “Optimal integration of energy storage in distribution networks,” 2009 IEEE Bucharest PowerTech, pp. 1–7, 2009.
[21]	J. Morren, S. Member, S. W. H. De Haan, W. L. Kling, and J. A. Ferreira, “Wind Turbines Emulating Inertia and Supporting Primary Frequency Control,” vol. 21, no. 1, pp. 2005–2006, 2006.
[22]	M. Swierczynski, R. Teodorescu, C. N. Rasmussen, P. Rodriguez, and H. Vikelgaard, “Overview of the energy storage systems for wind power integration enhancement,” 2010 IEEE Int. Symp. Ind. Electron., pp. 3749–3756, 2010.
[23]	I. Gyuk, S. Eckroad, and T. Key, “EPRI-DOE handbook supplement of energy storage for grid connected wind generation applications,” EPRI-DOE Rep., 2004.
[24]	T. Zhang, Z. J. Bao, G. Chen, Q. Yang, and W. J. Yan, “Control strategy for a hybrid energy storage system to mitigate wind power fluctuations,” 2013 6th Int. Conf. Adv. Comput. Intell. ICACI 2013 - Proc., vol. 28, no. 1, pp. 27–32, 2013.
[25]	H. Chen, T. N. Cong, W. Yang, C. Tan, Y. Li, and Y. Ding, “Progress in electrical energy storage system: A critical review,” Prog. Nat. Sci., vol. 19, no. 3, pp. 291–312, 2009.
[26]	W. Li, G. Jo??s, and C. Abbey, “Wind power impact on system frequency deviation and an ESS based power filtering algorithm solution,” 2006 IEEE PES Power Syst. Conf. Expo. PSCE 2006 - Proc., vol. 2, pp. 2077–2084, 2006.
[27]	A. K. Yoon, H. S. Noh, and Y. S. Yoon, “Analysis of Vanadium Redox Flow Battery Cell with Superconducting Charging System for Solar Energy,” Electr. Electron. Eng., vol. 6, no. 1, pp. 1–5, 2016.
[28]	D. L. Yao, S. S. Choi, K. J. Tseng, and T. T. Lie, “Determination of short-term power dispatch schedule for a wind farm incorporated with dual-battery energy storage scheme,” IEEE Trans. Sustain. Energy, vol. 3, no. 1, pp. 74–84, 2012.
[29]	P. Palensky and D. Dietrich, “Demand side management: Demand response, intelligent energy systems, and smart loads,” IEEE Trans. Ind. Informatics, vol. 7, no. 3, pp. 381–388, 2011.
[30]	“Demand Response.” [Online]. Available: https://www.nwcouncil.org/energy/dr/home/. [Accessed: 19-Jun-2017].
[31]	A. Brooks, E. Lu, D. Reicher, C. Spirakis, and B. Weihl, “Demand dispatch,” IEEE Power Energy Mag., vol. 8, no. 3, pp. 20–29, 2010.
[32]	A. Beghi, L. Cecchinato, M. Rampazzo, and F. Simmini, “Energy efficient control of HVAC systems with ice cold thermal energy storage,” pp. 4808–4813, 2014.
[33]	U. S. E. I. Administration and U.S. Energy Information Administration, “Annual Energy Outlook,” p. http://www.eia.doe.gov/oiaf/aeo/index.html, 2017.
[34]	N. Lu, “An evaluation of the HVAC load potential for providing load balancing service,” IEEE Trans. Smart Grid, vol. 3, no. 3, pp. 1263–1270, 2012.
[35]	P. Test, “9 . ENERGY PERFORMANCE ASSESSMENT OF HVAC SYSTEMS,” pp. 115–121.
[36]	“Battery State of Charge Determination.” [Online]. Available: http://www.mpoweruk.com/soc.htm. [Accessed: 12-May-2017].
[37]	“Battery Life and How To Improve It.” [Online]. Available: http://www.mpoweruk.com/life.htm. [Accessed: 12-May-2017].
[38]	Y. Ma, A. Kelman, A. Daly, and F. Borrelli, “Predictive Control for Energy Efficient Buildings with Thermal Storage: Modeling, Stimulation, and Experiments,” IEEE Control Syst., vol. 32, no. 1, pp. 44–64, 2012.
[39]	K. Dasgupta, J. Hazra, S. Rongali, and M. Padmanaban, “Estimating return on investment for grid scale storage within the economic dispatch framework,” Proc. 2015 IEEE Innov. Smart Grid Technol. - Asia, ISGT ASIA 2015, 2016.
[40]	S. Storage, “Energy Storage Use Case : Distribution System Optimization via Substation Storage,” no. June 2009, 2016.
[41]	J. Eyer, “Electric Utility Transmission and Distribution Upgrade Deferral Benefits from Modular Electricity Storage,” Sandia Natl. Lab., no. June, 2009.