# CHAPTER 1
# INTRODUCTION
## Motivation For the Thesis
In today’s society, energy supply is one of the main interests and energy consumption is considered as an important parameter to analyze the level of development of a society. World’s total energy consumption has been increasing throughout the years and it is expected to grow by 45% in 2040 [1]⁠.
Since the industrial revolution, fossil fuels are remained as the main source of energy. However, negative impacts of these sources led the search for alternative methods to fulfill energy requirements. Climate change, which is the result of increasing greenhouse gases in the atmosphere, is the main concern about fossil fuels. Moreover, fossil fuels are non-renewable energy sources, so there is a limited supply.
Renewable energy generation has been growing rapidly, with wind power having the highest percentage. In 2015, wind energy was the most popular renewable energy source with 3.7% of the global electricity supply [2]⁠. Historical development of installed wind capacity over years can be observed in Fig. 1-1 [3]⁠. Annual installations of wind capacity have been in excess of 50 GW for the last three years and at the end of 2016, total installed wind power capacity has reached to 486.8 GW.

Fig. 1-1: Historical development of installed wind capacity globally [3]⁠
In Fig. 1-2 [3]⁠, market forecast of wind capacity is shown with the growth rate expectations for next 5 years. Cumulative capacity growth rate is expected to be over 10% and total wind capacity is expected to reach around 817 GW in 2021.

Fig. 1-2: Market forecast of wind capacity [3]⁠
In a similar way to global development, wind capacity in Turkey also has been increasing over years. Installed wind capacity over years in Turkey can be observed in Fig. 1-3 [4]⁠. With 1,387 MW installation last year, total wind capacity of Turkey is brought to 6,106 MW, which was enough to supply 7.3% of electricity demand of the country in 2016. Considering limited oil and gas reserves, Turkish government has set a national target of total wind power capacity to 20 GW by 2023 [3]⁠.

Fig. 1-3: Historical development of installed wind capacity in Turkey [4]⁠
Flexibility of power systems is defined as the ability of a power system to respond to changes in demand and supply over a range of operating conditions [5]⁠. All power systems contain some degree of flexibility, as variability and uncertainty are always an issue and systems are designed to match the supply and demand all the time. However, with the renewable generation integration into power systems, variability and uncertainty become a problem of generation side, in addition to load side of the systems.
Relation of power output of a wind turbine to wind speed can be expressed as follows:
({hat T}_{amb})^{t+1} = %alpha (T_amb)^{t} + %alpha (1-%alpha) (T_amb)^{t-1} + %alpha (1-%alpha)^2 (T_amb)^{t-2} +...	(1-1)
where:
P	power output (W)
%rho_air	air density (kg/m3)
A	swept area (m2)
v	wind speed (m/s)
C_p	power coefficients
As it can be observed from Eq. 1-1, power output of a wind turbine is highly dependent on wind speed and even small variations of wind speed can cause large fluctuations in power output. Due to intermittent nature of wind, high level penetration of wind energy brings uncertainty and variability into power systems and energy balance problem becomes harder to achieve.
In Fig. 1-4, 10 minutes interval power output measurements of a wind farm in Turkey is shown. Daily fluctuations of wind generation with steep rises and sudden drops can be recognized in this figure.

Fig. 1-4: Daily generation of a wind farm in Turkey
The impact of increasing wind power penetration level to stability and reliability of the power system can be summarized as follows [6]⁠:
- Reliability: Net-load variations can be tracked by Conventional Generators (CGs) at low level integration of wind power to the power system [7]⁠. However, increasing penetration of wind energy eventually affects the system reliability as wind power output fluctuations are not controllable and generally wind generation is not related to the demand pattern, which leads an increase on the difference between peak and off-peak periods. As a result, committed CGs cannot catch the sudden and large changes of wind power output.
- Stability: Wind Turbine Generators (WTGs) cannot provide large contributions to frequency support, unlike synchronous generators [8]⁠. Wind power output fluctuations will also weaken voltage stability of the grid due to generation and load mismatch [9]⁠.
Considering expected share of wind generation in overall electric power generation to grow significantly over the years, more flexibility in power systems will be required to handle with the negative impacts of wind power. In the near future, system flexibility needs which has been driven by variable demand up to this day, will begin to be driven by supply variability.
In conventional power systems, generators with fast start time, high ramp-up/down and low minimum up/down-times are used to provide flexibility. However, considering the impact of wind generation on power systems, alternative methods are needed to compensate emerging effects. For the integration of renewable energy into power system effectively, four main options are proposed to provide flexibility to the power systems: dispatchable generation, transmission and distribution expansion, demand-side management and energy storage [10]⁠.
## Aims of the Thesis
With the high level penetration of wind generation, power systems are affected negatively due to intermittent nature of wind. One of the effects of wind power integration over power systems is transmission and distribution (T&D) upgrade need over existing structures. Considering the high investment cost of upgrade, T&D upgrade deferral becomes very profitable in specific cases.
In Fig. 1-5, power output of a wind farm in Turkey is shown for one year period. Power levels of this wind farm is also provided in Fig. 1-6. As it can be observed from these figures, wind generation is highly variable with a high peak to average ratio. Considering a modest overload over T&D system, demand-side management and energy storage applications can be used for absorbing power above the capacity of T&D line or component and releasing the stored energy when the T&D capacity is suitable.

Fig. 1-5: Generation of a wind farm in Turkey over a year

Fig. 1-6: Generation levels of a wind farm in Turkey over a year
Energy storage systems (ESSs) and demand-side management (DSM) are two main methods that can be integrated into power systems to supply the additional flexibility. In this chapter, general background of the thesis is presented. Main characteristics and applications of ESSs and DSM are explained. T&D system upgrade deferral concept is also introduced at the end of this chapter.
In this thesis, demand-side management and energy storage applications are chosen for the T&D upgrade deferral applications. Economical analysis of T&D system upgrade deferral will be investigated in presence of wind generation.
## Outline of the Thesis
Outline of the thesis can be formed as follows:
- Chapter 2 explains the flexibility concept and gives a general idea of the impact of wind generation on power systems. Literature review on energy storage systems and demand-side management are also provided in this chapter.
- Chapter 3 presents the modeling of both energy storage and demand-side management elements. Approach of transmission line capacity is also introduced in this chapter.
- Chapter 4 illustrates the contribution of storage systems and demand-side management to economical aspects of transmission systems with the simulation results and evaluations.
- Chapter 5 concludes the study and possible future works on that subject are discussed.
# CHAPTER 2
# PROVIDING FLEXIBILITY INTO POWER SYSTEMS FOR WIND POWER INTEGRATION
## Introduction
The main concern about planning and operation of the power systems is maintaining the equilibrium between security and efficiency. With the increasing penetration of renewable generation into power systems, sustaining this equilibrium becomes a more complicated problem to be solved. In order to reduce the impacts of renewable generation into power systems, further flexibility is required.
For better understanding, impact of wind generation on net load can be observed in Fig. 2-1 [5]⁠. Here, net load represents the demand which will be supplied by the CGs when the wind generation is utilized. It can be observed that wind generation leads to steeper ramps, deeper turn downs and shorter peaks which affects CG operations.

Fig. 2-1: Impact of wind generation on net-load [5]⁠
## Energy Storage Systems (ESSs)
In a power system, energy demand must be supplied instantaneously to preserve stability and quality of the system, which decreases as an imbalance between supply and demand occurs. In addition, scheduling of power systems with varying net load profile decreases the overall efficiency because of the deviations from optimal generation spot.
Conventional power systems operate effectively without storage, but efficiency of the systems can be increased with the integration of ESSs. Additionally, ESSs can be used to reduce the effects of wind power integration and increase reliability and stability of the systems.
Considering the recent development and advances in energy storage technology, ESSs have become a suitable solution for the negative impacts of wind power integration. An ESS can be described in terms of the following properties [11]⁠:
Storage capacity (MWh) is the amount of energy that can be stored by the ESS.
Power rating (MW) is the rate of energy transfer per unit time which can be supplied or consumed by ESS.
Energy to power ratio (E2P) is the ratio of the ESS storage capacity to its power. ESSs with higher energy to power ratio can deliver power for longer periods. ESS applications for different E2P ratio are listed at Table 2.1 [11]⁠.
Energy density is the ratio of the ESS storage capacity to its volume. ESSs with higher energy density can be used for applications where the volume of storage system is limited.
Power density is the ratio of the ESS power to its volume. ESSs with high power density can be used for high power applications with short duration of power usage.
Specific energy is the ratio of the ESS energy capacity to its weight. ESSs with high specific energy can be used for application with high energy demand and weight limitations.
Table 2.1: ESS applications for different energy to power ratio [11]⁠
Energy to power ratio	seconds to minutes	daily	weekly to monthly
Applications	Primary/Secondary frequency control / Spinning reserve / Voltage control / Black start capability / Peak shaving / Island grids / Electromobility (Hybrid electric vehicle) / Uninterruptible power supply	Tertiary frequency control / Standing reserve / Load leveling / Island grids / Electromobility (Full electric vehicle) / Residential storage systems / Uninterruptible power supply	Storage for “Dark calm” periods / Island grids

Specific power is the ratio of the ESS power to its weight. ESSs with high specific power can be used for applications with high power demand and weight limitations.
Depth of Discharge (DoD) is the ratio of the amount of discharged energy to the energy capacity of ESS. DoD limitations are used for several ESS technologies, as full discharge of ESSs are not allowed for technical reasons.
State of Charge (SoC) is the ratio of the amount of remaining energy to the usable energy capacity of ESS.
Efficiency is the ratio of output energy to input energy of ESS. With increasing losses, efficiency of the ESSs decreases.
Self discharge is the energy loss of ESS due to internal processes at standby.
Start-up time is the time period between power request and first power delivery.
Ramp-up time is the time period required from zero to full power transition.
Ramp rate is the ratio of maximum power to ramp-up time.
Deployment/response time is the time period between power request and full power delivery. In Fig. 2-2 [11]⁠, time parameters of a storage system can be observed.

Fig. 2-2: Response time of a storage system [11]⁠
Full cycle is the complete discharging and charging process of ESS.
Equivalent full cycle is the overall energy throughput with any DoD per cycle divided by available capacity.
Cycle life is the number of full cycles that can be delivered by ESS under specified conditions before ESS cannot meet specified criteria.
Calendar life is the lifetime of ESS when it is not used.
While choosing the suitable ESS for a given power system, these given properties must be carefully analyzed. Storage capacity and power rating are two important parameters for these systems. Capacity rate can be determined by control and energy management procedures while power rate can be determined by the difference between supply and demand.
## Classification of ESSs
A widely-used classification of energy storage technologies is according to the form of energy used [12]⁠:
- Mechanical:
  - Pumped hydro storage (PHS)
  - Compressed air energy storage (CAES)
  - Flywheel energy storage (FES)
- Electrochemical:
  - Secondary batteries
  - Flow batteries
- Chemical:
  - Hydrogen storage
  - Natural gas storage
- Electrical:
  - Super capacitor
  - Superconducting magnetic energy storage (SMES)
- Thermal
ESSs can be also categorized according to duration and frequency of the power supply [11]⁠:
Short-term ESS
Short-term ESSs are used for instant energy supply. This type of ESSs are used mainly in primary and secondary frequency control and reactive power compensation applications. This storage systems have low energy to power ratio of minutes and high charging and discharging rates. Generally, charging/discharging cycles per day are very high for this systems.
Medium-term ESS
Medium-term ESSs are used for matching the demand fluctuations between day and night. This type of ESSs are used mainly in matching day/night fluctuations of demand. Energy to power ratio of this systems are typically several hours. This type of systems have typically one or two cycles per day.
Long-term ESS
Long-term ESSs are used for power supply during several days or weeks. These systems have very high energy to power ratio, and due to this high energy capacity and relatively low power, the number of full cycles per year is very few. This kind of systems can be used to overcome “dark calm” periods, which can be explained as power generation shortage of power systems with high renewable energy penetration.
Comparison of rated power energy content of different ESS technologies are shown in Fig. 2-3 [12]⁠. Common applications of ESSs and their requirements for these applications are summarized at Table 2.2 [13]⁠. A more detailed classification of ESS applications with descriptions is also listed at Table 2.3 [14]⁠.

Fig. 2-3: Comparison of storage technologies [12]⁠
Table 2.2: Applications of storage systems and their requirements [13]⁠
Application type	Example of application	Power rating	Response Time	Discharge Time
Long duration, / Frequent	Bulk energy storage, / Energy arbitrage	>10 MW	minutes	4-8 hours
Medium duration, / Fast response	Capacity credit, / Spinning reserve, / T&D support	1-10 MW	seconds to minutes	0.5-2 hours
Short duration, / Highly frequent	Frequency regulation, / RES integration, / Power quality	0.1-2 MW	milliseconds to seconds	<0.25 hours

Table 2.3: Definition of ESS applications [14]⁠
	Application	Description
Generation and System Level Applications	Wholesale Energy Services	Utility-scale storage systems for bidding into energy, capacity and ancillary services markets
	Renewable Integration	Utility-scale storage providing renewables time shifting, load and ancillary services for grid integration
	Stationary Storage for T&D Support	Systems for T&D system support, improving T&D system utilization factor, and T&D capital deferral
Transmission and Distribution System Applications	Transportable Storage for T&D Support	Transportable storage systems for T&D system support and T&D deferral at multiple sites as needed
	Distributed Energy Storage Systems	Centrally managed modular systems providing increased customer reliability, grid T&D support and potentially ancillary services
	Energy Services Company Aggregated Systems	Residential-customer-sited storage aggregated and centrally managed to provide distribution system benefits
	Commercial and Industrial Power Quality and Reliability	Systems to provide power quality and reliability to commercial and industrial customers

## ESS Applications for Wind Integration Support
ESS applications for wind integration support can be categorized as generation-side, grid-side and demand-side applications [6]⁠:
Generation-side Applications
Different from conventional power plants, wind farm power output cannot be controlled in a strict way as a result of stochastic nature of wind. Power intermittency, ramp rates and limiting wind power output are the main challenges coming along with wind power integration to the power systems [15]⁠. Looking from the generation-side to overall system, controllability of a wind farm can be increased with the usage of ESS.
  - Time shifting:
Wind power generation is a non-dispatchable source of electricity production and can only be forecasted with a limited certainty. The mismatch between wind power output with the demand pattern, e.g. high wind power generation during off-peak demand and vise versa, is a big challenge as the difference between the peak and off-peak periods of system net-load increases.
Energy storage technologies can be used to match the wind power generation with load cycles by storing extra energy during high wind power generation and releasing it later during peak demand periods.
In time shifting applications, huge amount of energy is required to be stored for long time periods, so it is important to consider energy capacity and energy to power ratio parameters of an ESS in these applications.
  - Output smoothing:
Wind power generation can have sudden drops and steep rises as a result of changing wind speed. System stability will be affected with the sudden power output changes which will create frequency and voltage fluctuations.
Power output of a wind farm can be smoothed out with energy storage technology applications, excess energy can be stored during instantaneous increase in power generation and released when output power drops suddenly.
Ramping capability of ESS is the most important parameter in these applications, as storage system must response the sudden changes at wind power output.
  - Transmission utilization efficiency:
Wind resources are often located in remote locations and transmission networks limitations becomes a serious problem to supply the energy demand, which is far from wind farm sites [16]⁠.
With the usage of energy storage technology, efficiency of transmission utilization can be increased by reducing congestion over the network. Additionally, transmission and distribution upgrades can be deferred or in some cases avoided at all with proper usage of ESS.
Grid-side Applications
Increasing wind power generation reduces the stability and reliability of the grid, because of the intermittent nature of these supplies. Considering the distributed generation of wind farms over the system, net variability of the entire grid is lower compared to the integration of single wind power plant, so overall requirement of services is less than considering grid-side applications.
Energy storage technology can be used to provide ancillary services to decrease the impact of wind power generation over system stability and reliability. Grid-side applications of ESS is listed according to response time of the systems at Table 2.4 [6]⁠.
Table 2.4 Grid-side applications of ESS [6]⁠
Application	Response time
Energy arbitrage / Load levelling	Hours to days
Reserves / Efficiency use of transmission network / Emergency power supplying / Black start	Minutes to hours
Frequency regulation	Seconds to minutes
Inertia emulation / Oscillation damping / Voltage support / Low Voltage Ride Through support	Less than a second

  - Energy arbitrage/load leveling:
In the electricity market, electricity price varies during peak and off-peak hours. Hourly variation of prices in Turkey can be observed in Fig. 2-4 [17]⁠, as an average of hourly prices in 2016.
By storing low-cost energy during off-peak periods and releasing stored energy during peak periods with the higher price can reduce the gap between the peak and off-peak prices [18]⁠.

Fig. 2-4: Average of hourly electricity prices in Turkey [17]⁠
  - Frequency regulation:Energy arbitrage/load leveling:
ESS can be used to provide frequency regulation to the wind farms by controlling active power output of storage with frequency deviation. Primary frequency control can be applied by using droop control in local systems. Active power output of ESS can be controlled according to frequency change on the grid [19]⁠. For secondary frequency control, an automatic control system can arrange the power outputs to response frequency deviations.
  - Inertia emulation:
Frequency changes in a power system can be reduced by increasing the grid inertia [8]⁠. The impact of sudden wind generation changes by increasing inertia of grid which can be done by controlling the active power output of ESS.
  - Oscillation damping:
Sudden power changes of wind farms can cause oscillations in an interconnected system which may led to synchronization loss of some machines [20]⁠. To damp the system oscillations caused by variable wind generation output, ESS can be installed to the system and so, system stability can be increased.
  - Voltage control support:
Voltage stability of the grid can decrease with the variable nature of wind generation output. ESS integration can increase reactive power support for voltage regulation by controlling full scale converter connected to the grid [20]⁠.
  - Low Voltage Ride Through (LVRT) support:
Today, LVRT capability of wind turbine generators (WTGs) are determined by grid codes. During severe grid faults, wind turbines should remain connected for reactive power support and in some situations maximum reactive power needs to be delivered by wind turbines. For such cases, ESS can support the power need by converters and control systems.
  - Reserve application:
For the stability and reliability of the system, emergency reserves are required as a result of forecast error of wind power output. Integration of ESS can be an option for the reserve applications.
  - Emergency power supply:
In the situation of a fatal failure, ESS can be used to energize the power system from a shut-down condition [21]⁠.
  - Transmission utilization efficiency:
ESS integration can increase the efficiency of transmission network usage and transmission and distribution costs can be reduced by deferral of network upgrade.
Demand-side Applications
Variable loads can be used as a Virtual Power Plant (VPP) considering huge amounts. With the combination of ESS and demand-side management, ancillary services can be provided using VPP.
## Demand-side Management (DSM)
## In a conventional power system, the balance between generation and demand is maintained by controlling a limited number of power plants. However, with the increasing penetration of renewable generation to the system, dispatch of generation capacity to provide the required services to follow the load profile becoming much more difficult.
## As an alternative way, controlling load side to increase flexibility of the power system gains popularity. With the help of global communication infrastructure and embedded systems, loads can be dispatched according to system needs [22]⁠.
With DSM, flexible loads can be scheduled considering the grid needs. If individual loads can be aggregated and controlled on command according to needs of power systems, the result will be the same as generation dispatch. For example, turning off a large number of loads when the demand exceeds generation will affect the system as if the generation is increased and vice versa.
## Classification of DSM
DSM is defined as all the applications which can be applied to the demand-side of the power system. DSM can be categorized according to timing and impact of the applications, which can be observed in Fig. 2-5 [22]⁠.

Fig. 2-5: Categories of DSM [22]⁠
Energy Efficiency (EE)
EE applications include increasing the efficiency of appliances and improvements on the system properties. Changing a refrigerator with a more efficient one or applying thermal insulation to a building are some examples that can be considered as EE applications. In addition, behavioral changes of users to increase efficiency of energy usage can be included in these applications.
Time of Use (TOU)
In time of use tariffs, electricity prices change according to power consumption at that time. At peak power consumption periods (17:00-22:00 for Turkey), electricity prices are much higher compared to the rest of the day. So, customers arrange their power consumption to reduce the overall cost.
Demand Response (DR)
DR is defined as controlling flexible loads to shift power consumption from peak periods to off-peak periods. By doing so, energy consumption is not decreased but only shifted through time. However, by shifting peak power consumption through time, the overall efficiency of power system is increased.
Impact of EE and DR applications over consumption can be observed in Fig. 2-6 [22]⁠.

Fig. 2-6: Impact of demand-side management applications [22]⁠
Spinning Reserve (SR)
Aggregated loads can be used for frequency regulation applications both for primary and secondary control. Primary frequency control is done by controlling active power considering frequency changes over time. In secondary frequency control, frequency is restored with additional active power to the system. With SR applications, combination of large number of loads can be controlled like a virtual power plant with negative power output to the grid.
## Applications of DSM
DSM applications can be classified according to the time scale of the load control [23]⁠:
Hours
Dispatchable loads can be controlled to match highly varying wind generation profile for a wind farm or even for a region, depending on the limits of aggregated loads. Rapid changes in wind power generation can be followed by DSM control, as the flexible loads generally have a fast response. With the usage of DSM into the power systems, the required fast-response generation capacity will be reduced.
Seconds to minute
The ancillary services for power system regulation is provided by power plants in today’s power systems. An alternative way for serving these services to the power system is DSM. By controlling high number of loads with fast response, regulation can be provided in an efficient way.
Under a second
Frequency changes in a system can be observed and dispatchable loads can respond to these changes to maintain system security. Either loads can be shut down when a steep frequency drop occurs on the grid, or they can response to frequency changes according to frequency error, similar like droop control of conventional power plants. As wind power plants cannot participate to droop control, demand dispatch can be a solution for the intermittent wind power output.
## T&D Upgrade Deferral
With the increasing generation and demand over power systems, existing T&D structures become insufficient over time and upgrade of present structures becomes inevitable. The main problem of upgrading existing T&D structures is the high investment cost. CAPEX of the T&D equipment that may be deferred for installation or replacement can be estimated from inventory analysis, system planning models and construction cost estimates. Each application is unique and dependent on the various effects, such as installation requirements and location.
However, by using suitable technologies, T&D upgrade can be deferred in specific conditions. Viability of T&D upgrade deferral can be examined by checking some criteria over present systems [24]⁠:
- High T&D investment cost
- High peak-to-average ratio on loading of T&D structures
- Modest projected overload
- Slow peak demand growth
- Uncertainty about timing and/or likelihood of block additions
- T&D construction delays or construction resource constraints
- T&D upgrade competes with other important projects for capital
For better understanding of this concept, a specific case is illustrated in Fig. 2-7 [24]⁠.
T&D upgrade factor is defined as the amount of carrying capacity to be added to the T&D system as part of the upgrade [24]⁠. Typical upgrade factor values range from 0.25 (%25 capacity addition) to 0.50. For this study, upgrade factor is defined as 0.25
In order to estimate the annual cost of utility capital equipment based on the total installed cost of the equipment, fixed charge rate is used. In this study, fixed charge rate is taken as 0.11 [24]⁠.

Fig. 2-7: Upgrade of T&D capacity
## Conclusion
# CHAPTER 3
# MODELING AND APPROACHES
## Wind Power
Wind power generation data are obtained from Monitoring and Forecasting System Development for Wind Generated Electrical Power in Turkey Project of TUBITAK MAM Energy Institute. Obtained data are analyzed and organized with R programming.
## Power Flow
For T&D upgrade deferral application, power over the transmission line must be kept in line capacity limits. Considering the limitations, power flow constraints can be expressed as:
-P_line^max <= P_wg^t + P_bess^t - P_oiz^t - P_hvac^t <= P_line^max
where:
P_line^max	maximum transmission line capacity (MW)
P_wg^t	wind power generation of wind farms at time t (MW)
P_oiz^t	power demand of organized industrial zones at time t (MW)
P_bess^t	BESS power output at time t (MW)
P_hvac^t	power demand of HVAC units at time t (MW)
## Modeling of BESS
## Operation Mode
BESS can operate in three modes; discharging, charging and idle. In charging mode, batteries are charged with the power drawn from grid and BESS can be considered as a load. In discharging mode, the power is supplied to the grid with discharge of the batteries and BESS can be considered as a generation unit. In idle mode, batteries are neither charged nor discharged. Mode variables of BESS are tabulated at Table 3.1 and stated as an equation.
Table 3.1: Mode variables of BESS
Variable	Idle mode	Discharging mode	Charging mode
u_dsch^t	0	1	0
u_ch^t	0	0	1

u_dsch^t + u_ch^t <= 1
where:
u_dsch^t	discharging mode indicator of BESS at time t
u_ch^t	charging mode indicator of BESS at time t
## Energy
SoC of a battery is defined as available capacity of the battery expressed as a percentage of its rated capacity. SoC is an indication of how longer a battery can continue to perform before recharging is needed [25]. SoC of a BESS can be expressed as:
SoC^{t+1} = SoC^{t} + {[ P_ch^t - P_dsch^t ]{{%DELTA T} over {60}}} over { S_cap }
S_cap = (E2P) P_{bess,rt }
where:
SoC^t	state of charge of BESS at time t
P_ch^t	power supplied to the BESS at time t (MW)
P_dsch^t	power drawn from BESS at time t (MW)
S_cap	storage capacity of BESS (MWh)
E2P	energy to power ratio of BESS (hours)
P_{bess,rt}	rated power of BESS (MW)
%DELTA T	time period (minutes)
Depleting or overcharging a battery is not desired, so proper limitations (i.e., 30%-100%) should be defined for SoC of the battery. SoC constraints can be expressed as:
SoC^min <= SoC^t <= SoC^max
where:
SoC^min	minimum allowed state of charge of BESS
SoC^max	maximum allowed state of charge of BESS
## Power
Discharging efficiency of a BESS is defined as the ratio of power supplied to grid to rate of change in stored energy in BESS. Charging efficiency of a BESS is defined as the ratio of rate of change in stored energy in BESS to power drawn from grid. Considering these definitions, power output of BESS can be expressed as:
P_bess^t = P_dsch^t { %eta_dsch} - P_ch^t {1 over %eta_ch}
where:
P_bess^t	BESS power output at time t (MW)
P_dsch^t	power drawn from BESS at time t (MW)
P_ch^t	power supplied to the BESS at time t (MW)
%eta_dsch	discharging efficiency of BESS
%eta_ch	charging efficiency of BESS
Battery charging and discharging powers are limited by the physical and chemical characteristics of the BESS. Limitations of charging and discharging powers of BESS can be expressed as:
0 <= P_dsch^t <= P_{bess,rt} u_dsch^t
0 <= P_ch^t <= P_{bess,rt} u_ch^t
where:
P_{ bess,rt}	rated power of BESS (MW)
P_dsch^t	power drawn from BESS at time t (MW)
P_ch^t	power supplied to the BESS at time t (MW)
(u_dsch)^t	discharging mode indicator of BESS at time t
(u_ch)^t	charging mode indicator of BESS at time t
Cost Equations
Capital expenditure (CAPEX) of a BESS is related to storage capacity of the BESS. CAPEX annuity of a BESS can be expressed as follows:
(CAPEX annuity)_BESS = CAPEX_BESS {{ IR (IR + 1)^L } over { (IR + 1)^L - 1 }}
CAPEX_BESS = (Stg) S^cap
where:
IR	interest rate (%/year)
L	lifetime period of BESS (years)
Stg	capital cost of BESS ($/MWh)
S^cap	storage capacity of BESS (MWh)
annual(OPEX(BESS)) = sum from{t=1} to {T}( Dschg P_dsch^t + Chg P_ch ^t ) * { {%DELTA T} over 60 }
where:
T	time instances in one year period
Dschg	discharging cost of BESS ($/MWh)
Chg	charging cost of BESS ($/MWh)
P_dsch^t	power drawn from the BESS at time t (MW)
P_ch^t	power supplied to the BESS at time t (MW)
%DELTA T	time period (minutes)
## Modeling of HVAC units
## Operation Mode
HVAC units can operate in three modes; cooling, heating and idle. In cooling mode, HVAC unit draws power from the grid to extract heat from the room. In heating mode, HVAC unit draws power from the grid to release heat to the room. In idle mode, HVAC unit neither cool nor heat the room. Mode variables of HVAC unit are tabulated at Table 3.2 and stated as an equation.
Table 3.2: Mode variables of HVAC unit
Variable	Idle mode	Cooling mode	Heating mode
(ucl)it	0	1	0
(uht)it	0	0	1

(u_cl)_i^t + (u_ht)_i^t <= 1
where:
(u_cl)_i^t	cooling mode indicator of HVACi at time t
(u_ht)_i^t	heating mode indicator of HVACi at time t
## Power
HVACs draw power from the grid both for cooling and heating modes. Total power drawn from the grid by HVACs can be expressed as follows:
P_hvac^t = sum from i=1 to N [(P_{hvac,rt})_i ((u_cl)_i^t + (u_ht)_i^t)]
where:
P_hvac^t	power demand of HVAC units at time t (kW)
(P_{hvac,rt})_i	rated power of HVACi at time t (kW)
(u_cl)_i^t	cooling mode indicator of HVACi at time t
(u_ht)_i^t	heating mode indicator of HVACi at time t
CoP for cooling mode is defined as the ratio of the removed heat to electrical input power and CoP for heating mode is defined as the ratio of the delivered heat to electrical input power [26]⁠. Considering these definitions, thermal power output of HVACs can be expressed as:
(Q_cl)^t_i = (CoP_cl)_i (P_{hvac,rt})_i (u_cl)_i^t
(Q_ht)^t_i = (CoP_ht)_i (P_{hvac,rt})_i (u_ht)_i^t
(P_{hvac,rt})_i	rated power of HVACi at time t (kW)
(CoP_cl)_i	coefficient of performance of HVACi for cooling
(CoP_ht)_i	coefficient of performance of HVACi for heating
(Q_cl)_i^t	equivalent cooling rate of HVACi at time t (kW)
(Q_ht)_i^t	equivalent heating rate of HVACi at time t (kW)
(u_cl)_i^t	cooling mode indicator of HVACi at time t
(u_ht)_i^t	heating mode indicator of HVACi at time t
Temperature Constraints
For modeling the HVAC unit, a simplified model for temperature dynamics of a space can be created using a resistance-capacitance (RC) circuit analogy [27]⁠. The simplified thermal mass model can be used for energy conversion problems, considering entire building and average temperature of all building spaces. Considering these approach, temperature of a building can be expressed as follows:
(T_room)_i^{t+1} = (T_room)_i^{t} + ({(T_out)_i^{t} - (T_room)_i^{t-1}} over {R_i C_i} + {(Q_ht)_i^t - (Q_cl)_i^t} over {C_i}) %DELTA t
where:
(T_room)_i^t	temperature of buildingi at time t (Co)
(T_out)_i^t	temperature of ambienti at time t (Co)
R_i	equivalent thermal resistance of buildingi (Co/kW)
C_i	equivalent heat capacity of buildingi (kJ/Co)
(Q_cl)_i^t	equivalent cooling rate of HVACi at time t (kW)
(Q_ht)_i^t	equivalent heating rate of HVACi at time t (kW)
Building temperature is controlled by the HVAC units and these limitations can be expressed as follows:
(T_room)_i^min < (T_room)_i^t < (T_room)_i^max
where:
(T_room)_i^t	temperature of buildingi at time t (Co)
(T_room)_i^min	minimum allowed temperature of buildingi (Co)
(T_room)_i^max	maximum allowed temperature of buildingi (Co)
# CHAPTER 4
# SIMULATIONS AND RESULTS
## Introduction
Ambient Temperature
For this thesis, ambient temperature data is collected from U.S. Climate Reference Network (USCRN) [28]⁠, as there is no accessible weather datasets of Turkey for sub hourly periods. In order to simulate suitable ambient temperature conditions for HVAC operations, USCRN monthly temperature data for 2016 are compared with the monthly temperature data collected from Turkish State Meteorological Service (TSMS) [29]⁠ for an area in Turkish Aegean Region between 1929-2016.. Monthly data of average temperature with minimum and maximum temperature averages taken from TSMS and USCRN are tabulated at Table 4.1 and Table 4.2, and collected data are plotted in Fig. 4-1 and Fig. 4-2, respectively.
Table 4.1: Summary of monthly temperature data taken from TSMS [29]⁠
	Average Temperature	Average Low Temperature	Average High Temperature
January	6.7	3.0	10.8
February	7.9	3.6	12.6
March	10.6	5.2	16.1
April	15.2	8.8	21.3
May	20.4	13.2	27
June	25.3	17.4	32.1
July	28.0	20.3	34.9
August	27.6	20.2	34.9
September	23.3	16.0	30.6
October	17.8	11.6	24.3
November	12.2	7.4	17.5
December	8.2	4.5	12.5

Fig. 4-1: Temperature of an area chosen from TSMS for one year period
Table 4.2: Summary of monthly temperature data taken from USCRN [28]⁠
	Average Temperature	Average Low Temperature	Average High Temperature
January	6.4	3.2	10.2
February	10.5	4.7	17.9
March	10.9	5.7	16.8
April	14.9	8.1	22.5
May	17.7	10.8	25.5
June	23.5	15.2	32.4
July	26.2	16.6	36.1
August	26.2	16.6	37.1
September	22.6	13.8	32.6
October	14.1	9.3	19.9
November	9.6	5.7	15.4
December	5.2	0.6	11.2

Fig. 4-2: Temperature of an area chosen from USCRN for one year period

Operation Mode of HVACs over a year
HVACs can operate in cooling or heating mode, depending on the ambient temperature. In order to determine operation mode of HVACs throughout the year, temperature data is divided into 12-hour periods.
By taking account the sunrise and sundown times throughout the year, days are separated into two equal periods; namely day period, between 07:00 to 19:00 and night period, between 19:00 to 07:00. In order to forecast the temperature of next period and determine the operation mode of HVACs accordingly, simple exponential smoothing method (SES) is used.
({hat T}_{amb})^{t+1} = %alpha (T_amb)^{t} + %alpha (1-%alpha) (T_amb)^{t-1} + %alpha (1-%alpha)^2 (T_amb)^{t-2} +...
where:
({hat T}_{amb})^{t+1}	ambient temperature forecast for time t+1
(T_amb)^t	ambient temperature at time t
%alpha	smoothing parameter
Average temperature for next HVAC operation period is forecasted using the average temperatures of last 14 HVAC operation periods (one week). Smoothing parameter is chosen as 0.7 and SES algorithm is done accordingly.
## Case 1
## Analysis of T&D Upgrade
It is assumed that wind farm is connected to near organized industrial zone through distribution line and overall system is connected to the transmission-side, as shown in Fig. 4-3. Transmission-side capacity is occupied by power flow from/to the grid (Pgrid), which is the difference between wind power generation and industrial load.

Fig. 4-3: System network

Grid

Pwind

Pgrid
Pload

Organized Industrial Zone
Wind Farm

In Fig. 4-4, wind generation (Pwind) and organize industrial load (Pload) for year 0 can be observed. Power flow on the transmission-side and histogram of power levels are given in Fig. 4-5 and Fig. 4-6, respectively. Summary of power flow is also tabulated at Table 4.3.

Fig. 4-4: Wind generation and industrial load (year 0)

Fig. 4-5: Power flow on transmission-side (year 0)

Fig. 4-6: Histogram of power flow on transmission-side
Table 4.3: Summary of power flow from/to grid
minimum	1st quarter	median	mean	3rd quarter	maximum
-25.93	-11.43	-4	-0.97	8.71	34.08

Transmission-side capacity for this system is chosen as 35 MW. Maximum power flow to the grids in the current year is 34.08 MW, 2.63% below the transmission-side capacity.
In order to analyze T&D upgrade deferral, different wind generation capacity installations to the existing wind farm are considered. Industrial demand growth is determined as 2% per year, for all scenarios.
With the defined parameters, annual cost of transmission-side is calculated as $1,203,125.
## BESS Integration
For transmission-side upgrade deferral, BESS integration to the wind farm at the common coupling point is considered, which is shown in Fig. 4-7.

Fig. 4-7: System network with BESS integration

Grid

Pwind

Pgrid
Pload

Organized Industrial Zone

Wind Farm

BESS

Pbess

Energy to power ratio of the BESS is chosen as 2 hours. Initial state of charge (SoC) of the BESS is defined as 0.9 and limited between 0.3 and 0.9.
Wind Power Increase of 4%
Necessary BESS storage capacity for this scenario is calculated as 1.2 MWh. Power flow from/to the grid before and after BESS integration to the wind farm is shown in Fig. 4-8. Power output and SoC of the BESS are also shown in Fig. 4-9 and Fig. 4-10, respectively. Technical specifications and annual cost of the BESS for this scenario is tabulated at Table 4.4.

Fig. 4-8: Power flow of transmission-side (%4 wind power generation increase)

Fig. 4-9: Power output of BESS (%4 wind power generation increase)

Fig. 4-10: SoC of BESS (%4 wind power generation increase)
Table 4.4: BESS results (%4 wind power generation increase)
Power rating (MW)	Storage Capacity (MWh)	Annual cost ($)
0.6	1.2	60,000.21

Wind Power Increase of 6%
Necessary BESS storage capacity for this scenario is calculated as 2.6 MWh. Power flow from/to the grid before and after BESS integration to the wind farm is shown in Fig. 4-11. Power output and SoC of the BESS are also shown in Fig. 4-12 and Fig. 4-13, respectively. Technical specifications and annual cost of the BESS for this scenario is tabulated at Table 4.5.

Fig. 4-11: Power flow of transmission-side (%6 wind power generation increase)

Fig. 4-12: Power output of BESS (%6 wind power generation increase)

Fig. 4-13: SoC of BESS (%6 wind power generation increase)
Table 4.5: BESS results (%6 wind power generation increase)
Power rating (MW)	Storage Capacity (MWh)	Annual cost ($)
1.3	2.6	130,001.5

Wind Power Increase of 8%
Necessary BESS storage capacity for this scenario is calculated as 10.8 MWh. Power flow from/to the grid before and after BESS integration to the wind farm is shown in Fig. 4-14. Power output and SoC of the BESS are also shown in Fig. 4-15 and Fig. 4-16, respectively. Technical specifications and annual cost of the BESS for this scenario is tabulated at Table 4.6.

Fig. 4-14: Power flow of transmission-side (%8 wind power generation increase)

Fig. 4-15: Power output of BESS (%8 wind power generation increase)

Fig. 4-16: SoC of BESS (%8 wind power generation increase)
Table 4.6: BESS results (%8 wind power generation increase)
Power rating (MW)	Storage Capacity (MWh)	Annual cost ($)
5.6	11.2	560,005.8

Wind Power Increase of 10%
Necessary BESS storage capacity for this scenario is calculated as 22 MWh. Power flow from/to the grid before and after BESS integration to the wind farm is shown in Fig. 4-17. Power output and SoC of the BESS are also shown in Fig. 4-18 and Fig. 4-19, respectively. Technical specifications and annual cost of the BESS for this scenario is tabulated at Table 4.7.

Fig. 4-17: Power flow of transmission-side (%10 wind power generation increase)

Fig. 4-18: Power output of BESS (%10 wind power generation increase)

Fig. 4-19: SoC of BESS (%10 wind power generation increase)
Table 4.7: BESS results (%10 wind power generation increase)
Power rating (MW)	Storage Capacity (MWh)	Annual cost ($)
11.6	23.2	1,160,014

## Demand-side Management Integration

Fig. 4-20:

Grid

Pwg

Pline
Poiz

Organized Industrial Zone
Wind Farm

Phvac

HVAC
(with DSM)

Fig. 4-21: Total power of HVACs without DSM

Fig. 4-22: Temperature control of HVACs without DSM
Wind Power Increase of 4%

Fig. 4-23: Total power of HVACs with DSM

Fig. 4-24: Temperature control of HVACs with DSM

Fig. 4-25: Power flow of transmission side

Wind Power Increase of 6%

Fig. 4-26: Total power of HVACs with DSM

Fig. 4-27: Temperature control of HVACs with DSM

Fig. 4-28: Power flow of transmission side

Wind Power Increase of 8%

Fig. 4-29: Total power of HVACs with DSM

Fig. 4-30: Temperature control of HVACs with DSM

Fig. 4-31: Power flow of transmission side

Wind Power Increase of 10%

Fig. 4-32: Total power of HVACs with DSM

Fig. 4-33: Temperature control of HVACs with DSM

Fig. 4-34: Power flow of transmission side
# CHAPTER 5
# CONCLUSION
REFERENCES

[1]	U.S. Energy Information Administration, International Energy Outlook 2016, vol. 0484(2016), no. May 2016. 2016.
[2]	“WIND IN NUMBERS | GWEC.” [Online]. Available: http://www.gwec.net/global-figures/wind-in-numbers/. [Accessed: 11-May-2017].
[3]	GWEC, “Global Wind Report 2016,” p. 76, 2017.
[4]	Turkish Wind Energy Association, “Türkiye Rüzgar Enerjisi İstatistik Raporu,” 2017.
[5]	J. Cochran et al., “Flexibility in 21st Century Power Systems,” 21st Century Power Partnersh., vol. May, p. 14, 2014.
[6]	H. Zhao, Q. Wu, S. Hu, H. Xu, and C. N. Rasmussen, “Review of energy storage system for wind power integration support,” Appl. Energy, vol. 137, pp. 545–553, 2015.
[7]	K. Dvijotham, S. Backhaus, and M. Chertkov, “Operations-Based Planning for Placement and Sizing of Energy Storage in a Grid With a High Penetration of Renewables,” vol. 98195, 2011.
[8]	Y. Sun, Z. Zhang, G. Li, and J. Lin, “Review on frequency control of power systems with wind power penetration,” Power Syst. Technol. ( …, pp. 1–8, 2010.
[9]	H. T. Le, S. Santoso, and T. Q. Nguyen, “Augmenting wind power penetration and grid voltage stability limits using ESS: Application design, sizing, and a case study,” IEEE Trans. Power Syst., vol. 27, no. 1, pp. 161–171, 2012.
[10]	“Commercialisation of Energy Storage in Europe,” no. March, p. 96, 2015.
[11]	G. Fuchs, B. Lunz, M. Leuthold, and D. U. Sauer, “Technology Overview on Electricity Storage,” Inst. Power Electron. Electr. Drives (ISEA), RWTH Aachen Univ., no. June, p. 66, 2012.
[12]	IEC, “Electrical Energy Storage - White Paper,” Int. Electrotech. Comm., 2011.
[13]	B. Zakeri and S. Syri, “Electrical energy storage systems: A comparative life cycle cost analysis,” Renew. Sustain. Energy Rev., vol. 42, pp. 569–596, 2015.
[14]	EPRI, “Electric Energy Storage Technology Options: A White Paper Primer on Applications, Costs and Benefits,” Epri, pp. 1–170, 2010.
[15]	S. Teleke, M. E. Baran, S. Member, S. Bhattacharya, and A. Q. Huang, “Optimal Control of Battery Energy Storage for Wind Farm Dispatching,” IEEE Trans. Energy Convers., vol. 25, no. 3, pp. 787–794, 2010.
[16]	“Advantages and Challenges of Wind Energy | Department of Energy.” [Online]. Available: https://energy.gov/eere/wind/advantages-and-challenges-wind-energy. [Accessed: 08-Jun-2017].
[17]	“ELEKTRİK PİYASASI,” 2016.
[18]	G. Celli, S. Mocci, F. Pilo, and M. Loddo, “Optimal integration of energy storage in distribution networks,” 2009 IEEE Bucharest PowerTech, pp. 1–7, 2009.
[19]	J. Morren, S. Member, S. W. H. De Haan, W. L. Kling, and J. A. Ferreira, “Wind Turbines Emulating Inertia and Supporting Primary Frequency Control,” vol. 21, no. 1, pp. 2005–2006, 2006.
[20]	M. Swierczynski, R. Teodorescu, C. N. Rasmussen, P. Rodriguez, and H. Vikelgaard, “Overview of the energy storage systems for wind power integration enhancement,” 2010 IEEE Int. Symp. Ind. Electron., pp. 3749–3756, 2010.
[21]	I. Gyuk, S. Eckroad, and T. Key, “EPRI-DOE handbook supplement of energy storage for grid connected wind generation applications,” EPRI-DOE Rep., 2004.
[22]	P. Palensky and D. Dietrich, “Demand side management: Demand response, intelligent energy systems, and smart loads,” IEEE Trans. Ind. Informatics, vol. 7, no. 3, pp. 381–388, 2011.
[23]	A. Brooks, E. Lu, D. Reicher, C. Spirakis, and B. Weihl, “Demand dispatch,” IEEE Power Energy Mag., vol. 8, no. 3, pp. 20–29, 2010.
[24]	J. Eyer, “Electric Utility Transmission and Distribution Upgrade Deferral Benefits from Modular Electricity Storage,” Sandia Natl. Lab., no. June, 2009.
[25]	“Battery State of Charge Determination.” [Online]. Available: http://www.mpoweruk.com/soc.htm. [Accessed: 12-May-2017].
[26]	“Cooling Load - Convert kW/ton to COP or EER.” [Online]. Available: http://www.engineeringtoolbox.com/cop-eer-d_409.html. [Accessed: 23-Jul-2017].
[27]	Y. Ma, A. Kelman, A. Daly, and F. Borrelli, “Predictive Control for Energy Efficient Buildings with Thermal Storage: Modeling, Stimulation, and Experiments,” IEEE Control Syst., vol. 32, no. 1, pp. 44–64, 2012.
[28]	H. J. Diamond et al., “U.S. climate reference network after one decade of operations status and assessment,” Bull. Am. Meteorol. Soc., vol. 94, no. 4, pp. 485–498, 2013.
[29]	“Meteoroloji Genel Müdürlüğü.” [Online]. Available: https://mgm.gov.tr/veridegerlendirme/il-ve-ilceler-istatistik.aspx. [Accessed: 31-Jul-2017].