# CHAPTER 1
# INTRODUCTION
## Motivation For the Thesis
In today’s society, energy supply is one of the main interests and energy consumption is considered as an important parameter to analyze the level of development of a society. World’s total energy consumption has been increasing throughout the years and it is expected to grow by 45% in 2040 [1]⁠.
Since the industrial revolution, fossil fuels are remained as the main source of energy. However, negative impacts of these sources led the search for alternative methods to fulfill energy requirements. Climate change, which is the result of increasing greenhouse gases in the atmosphere, is the main concern about fossil fuels. Moreover, fossil fuels are non-renewable energy sources, so there is a limited supply.
Renewable energy generation has been growing rapidly, with wind power having the highest percentage. Today, wind energy is the most popular renewable energy source with 3.7% of the global electricity supply and this percentage is expected to increase for the next years [2]⁠. At the end of 2016, total installed wind power capacity has reached to approximately 487 GW and is expected to reach around 790 GW in 2020 [3]⁠. Historical development of global installed wind capacity over years can be observed in can be observed in Fig. 1-1 [4]⁠.

Fig. 1-1: Historical development of installed wind capacity globally [4]⁠
In a similar way to global development, wind capacity in Turkey also has been increasing over years, which can be observed in Fig. 1-2 [5]⁠. Top 10 countries with new installed wind capacity in 2016 are listed in Fig. 1-3 [4]⁠. With 1,387 MW installation, Turkey has the 2.5% share of overall wind capacity installation in 2016.

Fig. 1-2: Historical development of installed wind capacity in Turkey [5]⁠

Fig. 1-3: Top 10 new installed wind capacity share among countries in 2016 [4]⁠
Relation of power output of a wind turbine to wind speed can be expressed as follows:
P = {1} over {2} %rho_air A v^3 C_p
where:
P	power output (W)
%rho_air	air density (kg/m3)
A	swept area (m2)
v	wind speed (m/s)
C_p	power coefficient
As it can be observed from Equation X, power output of a wind turbine is highly dependent on wind speed and even small variations of wind speed can cause large fluctuations in power output. Due to intermittent nature of wind, high level penetration of wind energy brings uncertainty and variability into power systems and energy balance problem becomes harder to achieve. Considering expected share of wind generation in overall electric power generation to grow significantly over the years, more flexibility in power systems will be required to handle with the negative impacts of wind power. In the near future, system flexibility needs which has been driven by variable demand up to this day, will begin to be driven by supply variability.
In Fig. 1-4, 10 minutes interval power output measurements of a wind farm in Turkey is shown. Daily fluctuations of wind generation with steep rises and sudden drops can be recognized in this figure.

Fig. 1-4: Daily generation of a wind farm in Turkey
The impact of increasing wind power penetration level to stability and reliability of the power system can be summarized as follows [6]⁠:
- Reliability: Net load variations can be tracked by Conventional Generators (CGs) at low level integration of wind power to the power system [7]⁠. However, increasing penetration of wind energy eventually affects the system reliability as wind generation is generally not related to the demand pattern, which leads to an increase on the net load difference between peak and off-peak periods. As a result, committed CGs cannot catch the sudden and large changes of wind power output.
- Stability: Wind Turbine Generators (WTGs) cannot provide large contributions to frequency support unlike synchronous generators [8]⁠. Wind power output fluctuations will also weaken voltage stability of the grid due to generation and load mismatch [9]⁠.
For the integration of renewable energy into power system effectively, four main options are proposed to provide flexibility to the power systems: dispatchable generation, transmission and distribution expansion, demand side management and energy storage [10]⁠.
## Aims of the Thesis
With the high level penetration of wind generation, power systems are affected negatively due to intermittent nature of wind. One of the effects of wind power integration over power systems is transmission and distribution (T&D) upgrade need over existing structures.

In this thesis, effects of demand side management and energy storage applications over a grid, which consists of a wind farm and organized industrial zone, will be analyzed. T&D upgrade deferral conditions will be studied and results will be compared.
## Outline of the Thesis
Outline of the thesis can be formed as follows:
- Chapter 2 explains the flexibility concept and gives a general idea of the impact of wind generation on power systems. Literature review on energy storage systems and demand side management are also provided in this chapter.
- Chapter 3 presents the modeling of both energy storage and demand side management elements. Approach of transmission line capacity is also introduced in this chapter.
- Chapter 4 illustrates the contribution of storage systems and demand side management to economical aspects of transmission systems with the simulation results and evaluations.
- Chapter 5 concludes the study and possible future works on that subject are discussed.
# CHAPTER 2
# PROVIDING FLEXIBILITY INTO POWER SYSTEMS FOR WIND POWER INTEGRATION
## Introduction
The main concern about planning and operation of the power systems is maintaining the equilibrium between security and efficiency. With the increasing penetration of renewable generation into power systems, sustaining this equilibrium becomes a more complicated problem to be solved. In order to reduce the impacts of renewable generation into power systems, further flexibility is required.
Flexibility of power systems is defined as the ability of a power system to respond to changes in demand and supply over a range of operating conditions [11]⁠. All power systems contain some degree of flexibility, as variability and uncertainty are always an issue and systems are designed to match the supply and demand all the time. However, with the renewable generation integration into power systems, variability and uncertainty become a problem of generation side, in addition to load side of the systems.
For better understanding, impact of wind generation on net load can be observed in Fig. 2-1 [11]⁠. Here, net load represents the demand which will be supplied by the CGs when the wind generation is utilized. It can be observed that wind generation leads to steeper ramps, deeper turn downs and shorter peaks which affects CG operations.

Fig. 2-1: Impact of wind generation on net-load [11]⁠
In conventional power systems, generators with fast start time, high ramp-up/down and low minimum up/down-times are used to provide flexibility. However, considering the impact of renewable generation on power systems, alternative methods are needed to compensate emerging effects. Energy storage systems (ESSs) and demand side management (DSM) are two main methods that can be integrated into power systems to supply the additional flexibility.
In this chapter, general background of the thesis is presented. Main characteristics and applications of ESSs and DSM are explained and evaluated for the wind power integration.
## Wind Power Output

Fig. 2-2: Typical output of wind turbine versus wind speed
Typical output of a wind turbine with changing wind speed is shown in Fig. 2-2 [12]⁠. At low speeds, enough torque cannot be exerted by the wind to rotate the turbine blades. With increasing wind speed, at some point the turbine blades will overcome friction and begin to rotate. The speed at which the turbine begins to rotate is called cut-in speed.
Above cut-in speed, power output of the wind turbine rapidly increases. The power output reaches the maximum limit of the generator in some point, which is called rated power output. After this point, increase in wind speed does not affect the power output of the wind turbine, as the design of the turbine is arranged to limit the power output.
With increasing wind speed, the forces on the turbine also increase and at some point the rotor is brought to a standstill with a breaking system in order to prevent possible damage. This critical speed is called cut-out speed.
## Energy Storage Systems (ESSs)
In a power system, energy demand must be supplied instantaneously to preserve stability and quality of the system. Stability and quality of a power system decreases as an imbalance between supply and demand occurs. In addition, scheduling of power systems with varying net-load profile decreases the overall efficiency because of the deviations from optimal generation spot.
Conventional power systems operate effectively without storage, but efficiency of the systems can be increased with the integration of ESSs. Additionally, ESSs can be used to reduce the effects of wind power integration and increase reliability and stability of the systems.
Considering the recent development and advances in energy storage technology, ESSs have become a suitable solution for the negative impacts of wind power integration. An ESS can be described in terms of the following properties [13]⁠:
Storage Capacity (kWh) is the amount of energy that can be stored by the ESS.
Power Rating (kW) is the rate of energy transfer per unit time which can be supplied or consumed by ESS.
Energy to Power Ratio is the ratio of the ESS storage capacity to its power. ESSs with higher energy to power ratio can deliver power for longer periods. Suitable applications for ESSs according to their maximum charge/discharge duration at rated power are summarized at Table 2.1 [13]⁠.
Table 2.1: ESS applications for different energy to power ratio [13]⁠
Energy to power ratio	seconds to minutes	daily	weekly to monthly
Applications	Primary/Secondary frequency control / Spinning reserve / Voltage control / Black start capability / Peak shaving / Island grids / Electromobility (Hybrid electric vehicle) / Uninterruptible power supply	Tertiary frequency control / Standing reserve / Load leveling / Island grids / Electromobility (Full electric vehicle) / Residential storage systems / Uninterruptible power supply	Storage for “Dark calm” periods / Island grids

Energy density is the ratio of the ESS storage capacity to its volume. ESSs with higher energy density can be used for applications where the volume of storage system is limited.
Power density is the ratio of the ESS power to its volume. ESSs with high power density can be used for high power applications with short duration of power usage.
Specific energy is the ratio of the ESS energy capacity to its weight. ESSs with high specific energy can be used for application with high energy demand and weight limitations.
Specific power is the ratio of the ESS power to its weight. ESSs with high specific power can be used for applications with high power demand and weight limitations.
Depth of Discharge (DoD) is the ratio of the amount of discharged energy to the energy capacity of ESS. DoD limitations are used for several ESS technologies, as full discharge of ESSs are not allowed for technical reasons.
State of Charge (SoC) is the ratio of the amount of remaining energy to the usable energy capacity of ESS.
Efficiency is the ratio of output energy to input energy of ESS. With increasing losses, efficiency of the ESSs decreases.
Self discharge is the energy loss of ESS due to internal processes at standby.
Start-up time is the time period between power request and first power delivery.
Ramp-up time is the time period required from zero to full power transition.
Ramp rate is the ratio of maximum power to ramp-up time.
Deployment/response time is the time period between power request and full power delivery. In Fig. 2-4 [13]⁠, time parameters of a storage system can be observed.

Fig. 2-3: Response time of a storage system
Full cycle is the complete discharging and charging process of ESS.
Equivalent full cycle is the overall energy throughput with any DoD per cycle divided by available capacity.
Cycle life is the number of full cycles that can be delivered by ESS under specified conditions before ESS cannot meet specified criteria.
Calendar life is the lifetime of ESS when it is not used.
While choosing the suitable ESS for a given power system, these given properties must be carefully analyzed. Storage capacity and power rating are two important parameters for these systems. Capacity rate can be determined by control and energy management procedures while power rate can be determined by the difference between supply and demand.
## Classification of ESS
A widely-used classification of energy storage technologies is according to the form of energy used [14]⁠:
- Mechanical:
  - Pumped hydro storage (PHS)
  - Compressed air energy storage (CAES)
  - Flywheel energy storage (FES)
- Electrochemical:
  - Secondary batteries
  - Flow batteries
- Chemical:
  - Hydrogen storage
  - Natural gas storage
- Electrical:
  - Super capacitor
  - Superconducting magnetic energy storage (SMES)
- Thermal:
  - Sensible heat storage
  - Phase change materials (PCM)
ESSs can be also categorized according to duration and frequency of the power supply [13]⁠:
Short-term ESS
Short-term ESSs are used for instant energy supply. This type of ESSs are used mainly in primary and secondary frequency control and reactive power compensation applications. This storage systems have low energy to power ratio of minutes and high charging and discharging rates. Generally, charging/discharging cycles per day are very high for this systems.
Medium-term ESS
Medium-term ESSs are used for matching the demand fluctuations between day and night. Energy to power ratio of this systems are between 1 to 10 hours. This type of systems have typically one or two cycles per day.
Long-term ESS
Long-term ESSs are used for power supply during several days or weeks. These systems have very high energy to power ratio, and due to this high energy capacity and relatively low power, the number of full cycles per year is very few.
Common applications of ESSs and their requirements for these applications are summarized at Table 2.2 [15]⁠. A more detailed classification of ESS applications with descriptions is also listed at Table 2.3 [16]⁠.
Table 2.2: Applications of storage systems and their requirements [15]⁠
Application type	Example of application	Power rating	Response Time	Discharge Time
Long duration, / Frequent	Bulk energy storage, / Energy arbitrage	>10 MW	minutes	4-8 hours
Medium duration, / Fast response	Capacity credit, / Spinning reserve, / T&D support	1-10 MW	seconds to minutes	0.5-2 hours
Short duration, / Highly frequent	Frequency regulation, / RES integration, / Power quality	0.1-2 MW	milliseconds to seconds	<0.25 hours

Table 2.3: Definition of ESS applications [16]⁠
	Application	Description
Generation and System Level Applications	Wholesale Energy Services	Utility-scale storage systems for bidding into energy, capacity and ancillary services markets
	Renewable Integration	Utility-scale storage providing renewables time shifting, load and ancillary services for grid integration
	Stationary Storage for T&D Support	Systems for T&D system support, improving T&D system utilization factor, and T&D capital deferral
Transmission and Distribution System Applications	Transportable Storage for T&D Support	Transportable storage systems for T&D system support and T&D deferral at multiple sites as needed
	Distributed Energy Storage Systems	Centrally managed modular systems providing increased customer reliability, grid T&D support and potentially ancillary services
	Energy Services Company Aggregated Systems	Residential-customer-sited storage aggregated and centrally managed to provide distribution system benefits
	Commercial and Industrial Power Quality and Reliability	Systems to provide power quality and reliability to commercial and industrial customers

## ESS Applications for Wind Integration Support
ESS applications for wind integration support can be categorized according to different stakeholders [6]⁠:
Generation-side Applications
Different from conventional power plants, wind farm power output cannot be controlled in a strict way as a result of stochastic nature of wind. Power intermittency, ramp rates and limiting wind power output are the main challenges coming along with wind power integration to the power systems [17]⁠. Looking from the generation-side to overall system, controllability of a wind farm can be increased with the usage of ESS.
  - Time shifting:
Wind power generation is a non-dispatchable source of electricity production and can only be forecasted with a limited certainty. The mismatch between wind power output with the demand pattern, e.g. high wind power generation during off-peak demand and vise versa, is a big challenge as the difference between the peak and off-peak periods of system net-load increases.
Energy storage technologies can be used to match the wind power generation with load cycles by storing extra energy during high wind power generation and releasing it later during peak demand periods.
In time shifting applications, huge amount of energy is required to be stored for long time periods, so it is important to consider energy capacity and energy to power ratio parameters of an ESS in these applications.
  - Output smoothing:
Wind power generation can have sudden drops and steep rises as a result of changing wind speed. System stability will be affected with the sudden power output changes which will create frequency and voltage fluctuations.
Power output of a wind farm can be smoothed out with energy storage technology applications, excess energy can be stored during instantaneous increase in power generation and released when output power drops suddenly.
Ramping capability of ESS is the most important parameter in these applications, as storage system must response the sudden changes at wind power output.
  - Transmission utilization efficiency:
Wind resources are often located in remote locations and transmission networks limitations becomes a serious problem to supply the energy demand, which is far from wind farm sites [18]⁠.
With the usage of energy storage technology, efficiency of transmission utilization can be increased by reducing congestion over the network. Additionally, transmission and distribution upgrades can be deferred or in some cases avoided at all with proper usage of ESS.
Grid-side Applications
Increasing wind power generation reduces the stability and reliability of the grid, because of the intermittent nature of these supplies. Considering the distributed generation of wind farms over the system, net variability of the entire grid is lower compared to the integration of single wind power plant, so overall requirement of services is less than considering grid-side applications.
Energy storage technology can be used to provide ancillary services to decrease the impact of wind power generation over system stability and reliability. Grid-side applications of ESS is listed according to response time of the systems at Table 2.4 [6]⁠.
Table 2.4 Grid-side applications of ESS [6]⁠
Application	Response time	Example
Energy arbitrage, / Load leveling	Hours to days	PHS, NaS, CAES, VRB
Frequency regulation	Seconds to minutes	Li-ion, NaS, FES, VRB
Inertia emulation, / Oscillation damping, / Voltage support, / LVRT	Less than a second	LA, NaS, FES, VRB
Reserves	Minutes to hours	PHS, FES, BESS
Efficiency use of transmission network	Minutes to hours	Li-ion
Emergency power supplying / Black start	Minutes to hours	LA

  - Energy arbitrage/load leveling
In the electricity market, electricity price varies during peak and off-peak hours. Hourly variation of prices in Turkey can be observed in Fig. 2-4 [19]⁠, as an average of hourly prices in 2016.
By storing low-cost energy during off-peak periods and releasing stored energy during peak periods with the higher price can reduce the gap between the peak and off-peak prices [20]⁠.

Fig. 2-4 Average of hourly electricity prices in Turkey [19]⁠
  - Frequency regulation
ESS can be used to provide frequency regulation to the wind farms by controlling active power output of storage with frequency deviation. Primary frequency control can be applied by using droop control in local systems. Active power output of ESS can be controlled according to frequency change on the grid [21]⁠. For secondary frequency control, an automatic control system can arrange the power outputs to response frequency deviations.
  - Inertia emulation
Frequency changes in a power system can be reduced by increasing the grid inertia [8]⁠. The impact of sudden wind generation changes by increasing inertia of grid which can be done by controlling the active power output of ESS.
  - Oscillation damping
Sudden power changes of wind farms can cause oscillations in an interconnected system which may led to synchronization loss of some machines [22]⁠. To damp the system oscillations caused by variable wind generation ouput, ESS can be installed to the system and so, system stability can be increased.
  - Voltage control support
Voltage stability of the grid can decrease with the variable nature of wind generation output. ESS integration can increase reactive power support for voltage regulation by controlling full scale converter connected to the grid [22]⁠.
  - Low Voltage Ride Through (LVRT) support
Today, LVRT capability of wind turbine generators (WTGs) are determined by grid codes. During severe grid faults, wind turbines should remain connected for reactive power support and in some situations maximum reactive power needs to be delivered by wind turbines. For such cases, ESS can support the power need by converters and control systems.
  - Reserve application
For the stability and reliability of the system, emergency reserves are required as a result of forecast error of wind power output. Integration of ESS can be an option for the reserve applications.
  - Emergency power supply
In the situation of a fatal failure, ESS can be used to energize the power system from a shut-down condition [23]⁠.
  - Transmission utilization efficiency
ESS integration can increase the efficiency of transmission network usage and transmission and distribution costs can be reduced by deferral of network upgrade.
demand side Applications
Variable loads can be used as a Virtual Power Plant (VPP) considering huge amounts. With the combination of ESS and demand side management, ancillary services can be provided using VPP.
## ESS Planning for Wind Power Integration Applications
Technical requirements of the ESS, such as power and energy capacity and charging/discharging duration range can be determined by analyzing characteristics of a wind farm.
Fluctuations of wind generation output at different time scales is an important parameter for ESS selection. Generation reserve and energy dispatch of the system is related to low frequency fluctuations (minutes to hours). On the other hand, power system frequency control is affected with high frequency fluctuations (seconds to minutes) [24]⁠.
High frequency fluctuations on the wind power output has an insignificant effect overall [25]⁠ and can be damped out by inertia of the turbine generator [26]⁠. As a result, it is required that ESS can be charged/discharged at full power capacity in hours for wind integration support [6]⁠.
Considering increasing rating capacity of wind farms, large-scale energy storage technologies are required for wind integration applications. As can be seen in Fig. 2-5 [27]⁠, BESS, PHS and CAES technologies are suitable for these applications, which can store energy for long periods at a high power rating. Among these three technologies, BESS is more suitable for the purpose, as PHS and CAES are limited by topographical constraints [28]⁠.

Fig. 2-5: Comparison of storage technologies [27]⁠
By taking account of the findings mentioned above and rapid development in battery technology and cost reduction, it is decided to study the BESS technology for the wind power applications.
Energy capacity and power ratings are the main parameters to be determined for the wind power applications of storage systems. ESS size determination can be modeled as an optimization problem considering application purpose, control strategy and economical aspects [6]⁠.
## Demand side Management (DSM)
## In a conventional power system, the balance between generation and demand is maintained by controlling a limited number of power plants. However, with the increasing penetration of renewable generation to the system, dispatch of generation capacity to provide the required services to follow the load profile becoming much more difficult.
## As an alternative way, controlling load side to increase flexibility of the power system gains popularity. With the help of global communication infrastructure and embedded systems, loads can be dispatched according to system needs [29]⁠.
With demand side management (DSM), flexible loads can be scheduled considering the grid needs. If individual loads can be aggregated and controlled on command according to needs of power systems, the result will be the same as generation dispatch. For example, turning off a large number of loads when the demand exceeds generation will affect the system as if the generation is increased and vice versa.
## Classification of DSM
DSM is defined as all the applications which can be applied to the demand side of the power system. DSM can be categorized according to timing and impact of the applications, which can be observed in Fig. 2-6 [29]⁠.

Fig. 2-6: Categories of DSM [29]⁠
Energy Efficiency (EE)
EE applications include increasing the efficiency of appliances and improvements on the system properties. Changing a refrigerator with a more efficient one or applying thermal insulation to a building are some examples that can be considered as EE applications. In addition, behavioral changes of users to increase efficiency of energy usage can be included in these applications.
Time of Use (TOU)
In time of use tariffs, electricity prices change according to power consumption at that time. At peak power consumption periods (17:00-22:00 for Turkey), electricity prices are much higher compared to the rest of the day. So, customers arrange their power consumption to reduce the overall cost.
Demand Response (DR)
DR is defined as controlling flexible loads to shift power consumption from peak periods to off-peak periods. By doing so, energy consumption is not decreased but only shifted through time. However, by shifting peak power consumption through time, the overall efficiency of power system is increased. Impact of DR applications can be seen in [30]⁠.

Fig. 2-7: Impact of DR application [30]⁠
Spinning Reserve (SR)
Aggregated loads can be used for frequency regulation applications both for primary and secondary control. Primary frequency control is done by controlling active power considering frequency changes over time. In secondary frequency control, frequency is restored with additional active power to the system. With SR applications, combination of large number of loads can be controlled like a virtual power plant with negative power output to the grid.
## Applications of DSM
DSM applications can be classified according to the time scale of the load control [31]⁠:
Hours
Dispatchable loads can be controlled to match highly varying wind generation profile for a wind farm or even for a region, depending on the limits of aggregated loads. Rapid changes in wind power generation can be followed by DSM control, as the flexible loads generally have a fast response. With the usage of DSM into the power systems, the required fast-response generation capacity will be reduced.
Seconds to minute
The ancillary services for power system regulation is provided by power plants in today’s power systems. An alternative way for serving these services to the power system is DSM. By controlling high number of loads with fast response, regulation can be provided in an efficient way.
Under a second
Frequency changes in a system can be observed and dispatchable loads can respond to these changes to maintain system security. Either loads can be shut down when a steep frequency drop occurs on the grid, or they can response to frequency changes according to frequency error, similar like droop control of conventional power plants. As wind power plants cannot participate to droop control, demand dispatch can be a solution for the intermittent wind power output.
## DSM Planning for Wind Power Integration Applications
DSM takes advantage of controllable loads and support the grid considering changing needs, so in order to dispatch loads, some flexibility is needed in demand side. Flexible loads can be categorized by their impact to the end-user [31]⁠:
- Controlling some loads can affect the comfort of end-user, e.g. lights, air conditioning.
- Some loads can be controlled and affect end-user slightly or not at all, e.g. charging a plug-in vehicle at night.
Some suitable loads for DSM applications can be listed as follows [31]⁠:
- dishwashers
- washers and dryers
- electric hot water heaters
- Heating, ventilation and air-conditioning (HVAC) systems
- battery charges for consumer electronics
- plug-in vehicles
Considering the large number of aggregated flexible loads, demand dispatch can be an important factor for the power systems applications. However, there are some constraints for the flexible loads such as minimum and maximum power limits which they can draw from the grid and maximum energy drawing capacity.
Some important parameters must be defined for each individual load, such as minimum and maximum power limits, how much and when energy is needed and number of cycles for a given time period. The main objective of demand dispatch is to serve the grid needs by dispatching loads while considering these limitations. Suitable services for the power systems can be developed by considering power and energy limitations of flexible loads as well as their response characteristics.
HVAC systems are chosen to be controlled in simulations in this study, as they are responsible for a high percentage of energy usage in residential, commercial and industrial sectors [32]⁠. End-use energy consumption for residential and commercial sectors can be observe in Fig. 2-8 [33]⁠.

Fig. 2-8: End-use energy consumption for residential and commercial sectors [33]⁠
Thermal behavior of a HVAC unit can be seen in Fig. 2-9 [34]⁠. With suitable control methods, HVAC systems, when aggregated, can participate in matching generation and load, as well as ancillary services to support grid.

Fig. 2-9: Thermal behavior of a HVAC unit [34]⁠
A HVAC can be described in terms of the following properties [35]⁠:
Coefficient of Performance (CoP) is the HVAC efficiency measured in cooling/heating output divided by electrical power input.
Energy Efficiency Ratio (EER) is the ratio of cooling/heating capacity of HVAC to electrical power input at full-load conditions.
Two control methods can be used for DSM applications of HVAC systems: indirect load control and direct load control; indirect load control and direct load control [34]⁠.
Indirect load control: Customers (manually) or appliances (automatically) control the loads according to the specific requirements, e.g. frequency deviation in power systems.
Direct load control: Loads are controlled directly by an operator, without considering end-user priorities.
As mentioned in [34]⁠, direct load control is more controllable and observable compared to indirect control. Considering this, direct load control is applied for controlling HVACs in this study.
## Conclusion
# CHAPTER 3
# MODELING AND APPROACHES
## Wind Power
Wind power generation data are obtained from Monitoring and Forecasting System Development for Wind Generated Electrical Power in Turkey Project of TUBITAK MAM Energy Institute. Obtained data are analyzed and organized with R programming.
## Power Flow
For T&D upgrade deferral application, power over the transmission line must be kept in line capacity limits. Considering the limitations, power flow constraints can be expressed as:
-P_line^max <= P_wg^t + P_bess^t - P_oiz^t - P_hvac^t <= P_line^max
where:
P_line^max	maximum transmission line capacity (MW)
P_wg^t	wind power generation of wind farms at time t (MW)
P_oiz^t	power demand of organized industrial zones at time t (MW)
P_bess^t	BESS power output at time t (MW)
P_hvac^t	power demand of HVAC units at time t (MW)
## Modeling of BESS
## Operation Mode
BESS can operate in three modes; discharging, charging and idle. In charging mode, batteries are charged with the power drawn from grid and BESS can be considered as a load. In discharging mode, the power is supplied to the grid with discharge of the batteries and BESS can be considered as a generation unit. In idle mode, batteries are neither charged nor discharged. Mode variables of BESS are tabulated at Table 3.1 and stated as an equation.
Table 3.1: Mode variables of BESS
Variable	Idle mode	Discharging mode	Charging mode
u_dsch^t	0	1	0
u_ch^t	0	0	1

u_dsch^t + u_ch^t <= 1
where:
u_dsch^t	discharging mode indicator of BESS at time t
u_ch^t	charging mode indicator of BESS at time t
## Energy
SoC of a battery is defined as available capacity of the battery expressed as a percentage of its rated capacity. SoC is an indication of how longer a battery can continue to perform before recharging is needed [36]. SoC of a BESS can be expressed as:
SoC^{t+1} = SoC^{t} + {[ P_ch^t - P_dsch^t ]{{%DELTA T} over {60}}} over { S_cap }
S_cap = (E2P) P_{bess,rt }
where:
SoC^t	state of charge of BESS at time t
P_ch^t	power supplied to the BESS at time t (MW)
P_dsch^t	power drawn from BESS at time t (MW)
S_cap	storage capacity of BESS (MWh)
E2P	energy to power ratio of BESS (hours)
P_{bess,rt}	rated power of BESS (MW)
%DELTA T	time period (minutes)
Depleting or overcharging a battery is not desired, so proper limitations (i.e., 30%-100%) should be defined for SoC of the battery. SoC constraints can be expressed as:
SoC^min <= SoC^t <= SoC^max
where:
SoC^min	minimum allowed state of charge of BESS
SoC^max	maximum allowed state of charge of BESS
## Power
Discharging efficiency of a BESS is defined as the ratio of power supplied to grid to rate of change in stored energy in BESS. Charging efficiency of a BESS is defined as the ratio of rate of change in stored energy in BESS to power drawn from grid. Considering these definitions, power output of BESS can be expressed as:
P_bess^t = P_dsch^t { %eta_dsch} - P_ch^t {1 over %eta_ch}
where:
P_bess^t	BESS power output at time t (MW)
P_dsch^t	power drawn from BESS at time t (MW)
P_ch^t	power supplied to the BESS at time t (MW)
%eta_dsch	discharging efficiency of BESS
%eta_ch	charging efficiency of BESS
Battery charging and discharging powers are limited by the physical and chemical characteristics of the BESS. Limitations of charging and discharging powers of BESS can be expressed as:
0 <= P_dsch^t <= P_{bess,rt} u_dsch^t
0 <= P_ch^t <= P_{bess,rt} u_ch^t
where:
P_{ bess,rt}	rated power of BESS (MW)
P_dsch^t	power drawn from BESS at time t (MW)
P_ch^t	power supplied to the BESS at time t (MW)
(u_dsch)^t	discharging mode indicator of BESS at time t
(u_ch)^t	charging mode indicator of BESS at time t
Cost Equations
Capital expenditure (CAPEX) of a BESS is related to storage capacity of the BESS. CAPEX annuity of a BESS can be expressed as follows:
(CAPEX annuity)_BESS = CAPEX_BESS {{ IR (IR + 1)^L } over { (IR + 1)^L - 1 }}
CAPEX_BESS = (Stg) S^cap
where:
IR	interest rate (%/year)
L	lifetime period of BESS (years)
Stg	capital cost of BESS ($/MWh)
S^cap	storage capacity of BESS (MWh)
annual(OPEX(BESS)) = sum from{t=1} to {T}( Dschg P_dsch^t + Chg P_ch ^t ) * { {%DELTA T} over 60 }
where:
T	time instances in one year period
Dschg	discharging cost of BESS ($/MWh)
Chg	charging cost of BESS ($/MWh)
P_dsch^t	power drawn from the BESS at time t (MW)
P_ch^t	power supplied to the BESS at time t (MW)
%DELTA T	time period (minutes)
## Modeling of HVAC units
## Operation Mode
HVAC units can operate in three modes; cooling, heating and idle. In cooling mode, HVAC unit draws power from the grid to extract heat from the room. In heating mode, HVAC unit draws power from the grid to release heat to the room. In idle mode, HVAC unit neither cool nor heat the room. Mode variables of HVAC unit are tabulated at Table 3.2 and stated as an equation.
Table 3.2: Mode variables of HVAC unit
Variable	Idle mode	Cooling mode	Heating mode
(ucl)it	0	1	0
(uht)it	0	0	1

(u_cl)_i^t + (u_ht)_i^t <= 1
where:
(u_cl)_i^t	cooling mode indicator of HVACi at time t
(u_ht)_i^t	heating mode indicator of HVACi at time t
## Power
HVACs draw power from the grid both for cooling and heating modes. Total power drawn from the grid by HVACs can be expressed as follows:
P_hvac^t = sum from i=1 to N [(P_{hvac,rt})_i ((u_cl)_i^t + (u_ht)_i^t)]
where:
P_hvac^t	power demand of HVAC units at time t (kW)
(P_{hvac,rt})_i	rated power of HVACi at time t (kW)
(u_cl)_i^t	cooling mode indicator of HVACi at time t
(u_ht)_i^t	heating mode indicator of HVACi at time t
CoP for cooling mode is defined as the ratio of the removed heat to electrical input power and CoP for heating mode is defined as the ratio of the delivered heat to electrical input power [37]⁠. Considering these definitions, thermal power output of HVACs can be expressed as:
(Q_cl)^t_i = (CoP_cl)_i (P_{hvac,rt})_i (u_cl)_i^t
(Q_ht)^t_i = (CoP_ht)_i (P_{hvac,rt})_i (u_ht)_i^t
(P_{hvac,rt})_i	rated power of HVACi at time t (kW)
(CoP_cl)_i	coefficient of performance of HVACi for cooling
(CoP_ht)_i	coefficient of performance of HVACi for heating
(Q_cl)_i^t	equivalent cooling rate of HVACi at time t (kW)
(Q_ht)_i^t	equivalent heating rate of HVACi at time t (kW)
(u_cl)_i^t	cooling mode indicator of HVACi at time t
(u_ht)_i^t	heating mode indicator of HVACi at time t
Temperature Constraints
For modeling the HVAC unit, a simplified model for temperature dynamics of a space can be created using a resistance-capacitance (RC) circuit analogy [38]⁠. The simplified thermal mass model can be used for energy conversion problems, considering entire building and average temperature of all building spaces. Considering these approach, temperature of a building can be expressed as follows:
(T_room)_i^{t+1} = (T_room)_i^{t} + ({(T_out)_i^{t} - (T_room)_i^{t-1}} over {R_i C_i} + {(Q_ht)_i^t - (Q_cl)_i^t} over {C_i}) %DELTA t
where:
(T_room)_i^t	temperature of buildingi at time t (Co)
(T_out)_i^t	temperature of ambienti at time t (Co)
R_i	equivalent thermal resistance of buildingi (Co/kW)
C_i	equivalent heat capacity of buildingi (kJ/Co)
(Q_cl)_i^t	equivalent cooling rate of HVACi at time t (kW)
(Q_ht)_i^t	equivalent heating rate of HVACi at time t (kW)
Building temperature is controlled by the HVAC units and these limitations can be expressed as follows:
(T_room)_i^min < (T_room)_i^t < (T_room)_i^max
where:
(T_room)_i^t	temperature of buildingi at time t (Co)
(T_room)_i^min	minimum allowed temperature of buildingi (Co)
(T_room)_i^max	maximum allowed temperature of buildingi (Co)
# CHAPTER 4
# SIMULATIONS AND RESULTS
## Introduction
In this chapter, impact of BESS and demand side management of HVAC systems on transmission-side upgrade deferral is studied.
Actual power generation data from wind farms and load data from organized industrial zones are used in simulations. R programming language is used for data analysis and missing data interpretation. It is assumed that wind power generation and load are forecasted without any error.
## BESS Cost Assumptions
CAPEX and OPEX of BESS is taken as $500/kWh and $0.2/MWh respectively [39]⁠.
## T&D Cost Assumptions
CAPEX of the T&D equipment that may be deferred for installation or replacement can be estimated from inventory analysis, system planning models and construction cost estimates. Each application is unique and dependent on the various effects, such as installation requirements and location [40]⁠. In this study, CAPEX for transmission-side upgrade of 1 MW is taken as $50,000/km.
Transmission-side length is chosen 25 km for this study.
T&D upgrade factor is defined as the amount of carrying capacity to be added to the T&D system as part of the upgrade [41]⁠. Typical upgrade factor values range from 0.25 (%25 capacity addition) to 0.50. For this study, upgrade factor is defined as 0.25
In order to estimate the annual cost of utility capital equipment based on the total installed cost of the equipment, fixed charge rate is used. In this study, fixed charge rate is taken as 0.11 [41]⁠.
## Case 1
## Analysis of T&D Upgrade
It is assumed that wind farm is connected to near organized industrial zone through distribution line and overall system is connected to the transmission-side, as shown in Fig. 4-1. Transmission-side capacity is occupied by power flow from/to the grid (Pgrid), which is the difference between wind power generation and industrial load.

Fig. 4-1: System network

Grid

Pwind

Pgrid
Pload

Organized Industrial Zone
Wind Farm

In Fig. 4-2, wind generation (Pwind) and organize industrial load (Pload) for year 0 can be observed. Power flow on the transmission-side and histogram of power levels are given in Fig. 4-3 and Fig. 4-4, respectively. Summary of power flow is also tabulated at Table 4.1.

Fig. 4-2: Wind generation and industrial load (year 0)

Fig. 4-3: Power flow on transmission-side (year 0)

Fig. 4-4: Histogram of power flow on transmission-side
Table 4.1: Summary of power flow from/to grid
minimum	1st quarter	median	mean	3rd quarter	maximum
-25.93	-11.43	-4	-0.97	8.71	34.08

Transmission-side capacity for this system is chosen as 35 MW. Maximum power flow to the grids in the current year is 34.08 MW, 2.63% below the transmission-side capacity.
In order to analyze T&D upgrade deferral, different wind generation capacity installations to the existing wind farm are considered. Industrial demand growth is determined as 2% per year, for all scenarios.
With the defined parameters, annual cost of transmission-side is calculated as $1,203,125.
## BESS Integration
For transmission-side upgrade deferral, BESS integration to the wind farm at the common coupling point is considered, which is shown in Fig. 4-5.

Fig. 4-5: System network with BESS integration

Grid

Pwind

Pgrid
Pload

Organized Industrial Zone

Wind Farm

BESS

Pbess

Energy to power ratio of the BESS is chosen as 2 hours. Initial state of charge (SoC) of the BESS is defined as 0.9 and limited between 0.3 and 0.9.

Wind Power Increase of 4%
Necessary BESS storage capacity for this scenario is calculated as 1.2 MWh. Power flow from/to the grid before and after BESS integration to the wind farm is shown in Fig. 4-6. Power output and SoC of the BESS are also shown in Fig. 4-7 and Fig. 4-8, respectively. Technical specifications and annual cost of the BESS for this scenario is tabulated at Table 4.2.

Fig. 4-6: Power flow of transmission-side (%4 wind power generation increase)

Fig. 4-7: Power output of BESS (%4 wind power generation increase)

Fig. 4-8: SoC of BESS (%4 wind power generation increase)
Table 4.2: BESS results (%4 wind power generation increase)
Power rating (MW)	Storage Capacity (MWh)	Annual cost ($)
0.6	1.2	60,000.21

Wind Power Increase of 6%
Necessary BESS storage capacity for this scenario is calculated as 2.6 MWh. Power flow from/to the grid before and after BESS integration to the wind farm is shown in Fig. 4-9. Power output and SoC of the BESS are also shown in Fig. 4-10 and Fig. 4-11, respectively. Technical specifications and annual cost of the BESS for this scenario is tabulated at Table 4.3.

Fig. 4-9: Power flow of transmission-side (%6 wind power generation increase)

Fig. 4-10: Power output of BESS (%6 wind power generation increase)

Fig. 4-11: SoC of BESS (%6 wind power generation increase)
Table 4.3: BESS results (%6 wind power generation increase)
Power rating (MW)	Storage Capacity (MWh)	Annual cost ($)
1.3	2.6	130,001.5

Wind Power Increase of 8%
Necessary BESS storage capacity for this scenario is calculated as 10.8 MWh. Power flow from/to the grid before and after BESS integration to the wind farm is shown in Fig. 4-12. Power output and SoC of the BESS are also shown in Fig. 4-13 and Fig. 4-14, respectively. Technical specifications and annual cost of the BESS for this scenario is tabulated at Table 4.4.

Fig. 4-12: Power flow of transmission-side (%8 wind power generation increase)

Fig. 4-13: Power output of BESS (%8 wind power generation increase)

Fig. 4-14: SoC of BESS (%8 wind power generation increase)
Table 4.4: BESS results (%8 wind power generation increase)
Power rating (MW)	Storage Capacity (MWh)	Annual cost ($)
5.6	11.2	560,005.8

Wind Power Increase of 10%
Necessary BESS storage capacity for this scenario is calculated as 22 MWh. Power flow from/to the grid before and after BESS integration to the wind farm is shown in Fig. 4-15. Power output and SoC of the BESS are also shown in Fig. 4-16 and Fig. 4-17, respectively. Technical specifications and annual cost of the BESS for this scenario is tabulated at Table 4.5.

Fig. 4-15: Power flow of transmission-side (%10 wind power generation increase)

Fig. 4-16: Power output of BESS (%10 wind power generation increase)

Fig. 4-17: SoC of BESS (%10 wind power generation increase)
Table 4.5: BESS results (%10 wind power generation increase)
Power rating (MW)	Storage Capacity (MWh)	Annual cost ($)
11.6	23.2	1,160,014

## Demand side Management Integration

Fig. 4-18:

Grid

Pwg

Pline
Poiz

Organized Industrial Zone
Wind Farm

Phvac

HVAC
(with DSM)

Fig. 4-19: Total power of HVACs without DSM

Fig. 4-20: Temperature control of HVACs without DSM
Wind Power Increase of 4%

Fig. 4-21: Total power of HVACs with DSM

Fig. 4-22: Temperature control of HVACs with DSM

Fig. 4-23: Power flow of transmission side

Wind Power Increase of 6%

Fig. 4-24: Total power of HVACs with DSM

Fig. 4-25: Temperature control of HVACs with DSM

Fig. 4-26: Power flow of transmission side

Wind Power Increase of 8%

Fig. 4-27: Total power of HVACs with DSM

Fig. 4-28: Temperature control of HVACs with DSM

Fig. 4-29: Power flow of transmission side
Wind Power Increase of 10%

Fig. 4-30: Total power of HVACs with DSM

Fig. 4-31: Temperature control of HVACs with DSM

Fig. 4-32: Power flow of transmission side
# CHAPTER 5
# CONCLUSION
REFERENCES

[1]	U.S. Energy Information Administration, International Energy Outlook 2016, vol. 0484(2016), no. May 2016. 2016.
[2]	“WIND IN NUMBERS | GWEC.” [Online]. Available: http://www.gwec.net/global-figures/wind-in-numbers/. [Accessed: 11-May-2017].
[3]	“Cumulative-Market-Forecast-by-Region-2016-2020-1.jpg (2091×1123).” [Online]. Available: http://www.gwec.net/wp-content/uploads/2016/04/Cumulative-Market-Forecast-by-Region-2016-2020-1.jpg. [Accessed: 11-May-2017].
[4]	GWEC, “Global Wind Statistics 2016,” Glob. Wind Stat. 2016, p. 4, 2017.
[5]	Turkish Wind Energy Association, “Türkiye Rüzgar Enerjisi İstatistik Raporu,” 2017.
[6]	H. Zhao, Q. Wu, S. Hu, H. Xu, and C. N. Rasmussen, “Review of energy storage system for wind power integration support,” Appl. Energy, vol. 137, pp. 545–553, 2015.
[7]	K. Dvijotham, S. Backhaus, and M. Chertkov, “Operations-Based Planning for Placement and Sizing of Energy Storage in a Grid With a High Penetration of Renewables,” vol. 98195, 2011.
[8]	Y. Sun, Z. Zhang, G. Li, and J. Lin, “Review on frequency control of power systems with wind power penetration,” Power Syst. Technol. ( …, pp. 1–8, 2010.
[9]	H. T. Le, S. Santoso, and T. Q. Nguyen, “Augmenting wind power penetration and grid voltage stability limits using ESS: Application design, sizing, and a case study,” IEEE Trans. Power Syst., vol. 27, no. 1, pp. 161–171, 2012.
[10]	“Commercialisation of Energy Storage in Europe,” no. March, p. 96, 2015.
[11]	J. Cochran et al., “Flexibility in 21st Century Power Systems,” 21st Century Power Partnersh., vol. May, p. 14, 2014.
[12]	A. Ipakchi and F. Albuyeh, “Grid of the future,” IEEE Power Energy Mag., vol. 7, no. 2, pp. 52–62, 2009.
[13]	G. Fuchs, B. Lunz, M. Leuthold, and D. U. Sauer, “Technology Overview on Electricity Storage,” Inst. Power Electron. Electr. Drives (ISEA), RWTH Aachen Univ., no. June, p. 66, 2012.
[14]	K. Han and T. Carson, “Executive summary,” Management, vol. II, pp. 10–16, 2008.
[15]	B. Zakeri and S. Syri, “Electrical energy storage systems: A comparative life cycle cost analysis,” Renew. Sustain. Energy Rev., vol. 42, pp. 569–596, 2015.
[16]	EPRI, “Electric Energy Storage Technology Options: A White Paper Primer on Applications, Costs and Benefits,” Epri, pp. 1–170, 2010.
[17]	S. Teleke, M. E. Baran, S. Member, S. Bhattacharya, and A. Q. Huang, “Optimal Control of Battery Energy Storage for Wind Farm Dispatching,” IEEE Trans. Energy Convers., vol. 25, no. 3, pp. 787–794, 2010.
[18]	“Advantages and Challenges of Wind Energy | Department of Energy.” [Online]. Available: https://energy.gov/eere/wind/advantages-and-challenges-wind-energy. [Accessed: 08-Jun-2017].
[19]	“ELEKTRİK PİYASASI,” 2016.
[20]	G. Celli, S. Mocci, F. Pilo, and M. Loddo, “Optimal integration of energy storage in distribution networks,” 2009 IEEE Bucharest PowerTech, pp. 1–7, 2009.
[21]	J. Morren, S. Member, S. W. H. De Haan, W. L. Kling, and J. A. Ferreira, “Wind Turbines Emulating Inertia and Supporting Primary Frequency Control,” vol. 21, no. 1, pp. 2005–2006, 2006.
[22]	M. Swierczynski, R. Teodorescu, C. N. Rasmussen, P. Rodriguez, and H. Vikelgaard, “Overview of the energy storage systems for wind power integration enhancement,” 2010 IEEE Int. Symp. Ind. Electron., pp. 3749–3756, 2010.
[23]	I. Gyuk, S. Eckroad, and T. Key, “EPRI-DOE handbook supplement of energy storage for grid connected wind generation applications,” EPRI-DOE Rep., 2004.
[24]	T. Zhang, Z. J. Bao, G. Chen, Q. Yang, and W. J. Yan, “Control strategy for a hybrid energy storage system to mitigate wind power fluctuations,” 2013 6th Int. Conf. Adv. Comput. Intell. ICACI 2013 - Proc., vol. 28, no. 1, pp. 27–32, 2013.
[25]	H. Chen, T. N. Cong, W. Yang, C. Tan, Y. Li, and Y. Ding, “Progress in electrical energy storage system: A critical review,” Prog. Nat. Sci., vol. 19, no. 3, pp. 291–312, 2009.
[26]	W. Li, G. Jo??s, and C. Abbey, “Wind power impact on system frequency deviation and an ESS based power filtering algorithm solution,” 2006 IEEE PES Power Syst. Conf. Expo. PSCE 2006 - Proc., vol. 2, pp. 2077–2084, 2006.
[27]	A. K. Yoon, H. S. Noh, and Y. S. Yoon, “Analysis of Vanadium Redox Flow Battery Cell with Superconducting Charging System for Solar Energy,” Electr. Electron. Eng., vol. 6, no. 1, pp. 1–5, 2016.
[28]	D. L. Yao, S. S. Choi, K. J. Tseng, and T. T. Lie, “Determination of short-term power dispatch schedule for a wind farm incorporated with dual-battery energy storage scheme,” IEEE Trans. Sustain. Energy, vol. 3, no. 1, pp. 74–84, 2012.
[29]	P. Palensky and D. Dietrich, “Demand side management: Demand response, intelligent energy systems, and smart loads,” IEEE Trans. Ind. Informatics, vol. 7, no. 3, pp. 381–388, 2011.
[30]	“Demand Response.” [Online]. Available: https://www.nwcouncil.org/energy/dr/home/. [Accessed: 19-Jun-2017].
[31]	A. Brooks, E. Lu, D. Reicher, C. Spirakis, and B. Weihl, “Demand dispatch,” IEEE Power Energy Mag., vol. 8, no. 3, pp. 20–29, 2010.
[32]	A. Beghi, L. Cecchinato, M. Rampazzo, and F. Simmini, “Energy efficient control of HVAC systems with ice cold thermal energy storage,” pp. 4808–4813, 2014.
[33]	U. S. E. I. Administration and U.S. Energy Information Administration, “Annual Energy Outlook,” p. http://www.eia.doe.gov/oiaf/aeo/index.html, 2017.
[34]	N. Lu, “An evaluation of the HVAC load potential for providing load balancing service,” IEEE Trans. Smart Grid, vol. 3, no. 3, pp. 1263–1270, 2012.
[35]	P. Test, “9 . ENERGY PERFORMANCE ASSESSMENT OF HVAC SYSTEMS,” pp. 115–121.
[36]	“Battery State of Charge Determination.” [Online]. Available: http://www.mpoweruk.com/soc.htm. [Accessed: 12-May-2017].
[37]	“Cooling Load - Convert kW/ton to COP or EER.” [Online]. Available: http://www.engineeringtoolbox.com/cop-eer-d_409.html. [Accessed: 23-Jul-2017].
[38]	Y. Ma, A. Kelman, A. Daly, and F. Borrelli, “Predictive Control for Energy Efficient Buildings with Thermal Storage: Modeling, Stimulation, and Experiments,” IEEE Control Syst., vol. 32, no. 1, pp. 44–64, 2012.
[39]	K. Dasgupta, J. Hazra, S. Rongali, and M. Padmanaban, “Estimating return on investment for grid scale storage within the economic dispatch framework,” Proc. 2015 IEEE Innov. Smart Grid Technol. - Asia, ISGT ASIA 2015, 2016.
[40]	S. Storage, “Energy Storage Use Case : Distribution System Optimization via Substation Storage,” no. June 2009, 2016.
[41]	J. Eyer, “Electric Utility Transmission and Distribution Upgrade Deferral Benefits from Modular Electricity Storage,” Sandia Natl. Lab., no. June, 2009.