# CHAPTER X
# FLEXIBILITY IN POWER SYSTEMS
For power systems, flexibility can be defined as the ability of the system to maintain the balance between generation and consumption over changing conditions. Variability and uncertainty are important issues for power systems, and to cover the deviations from equilibrium and unexpected situations, enough energy resources are needed. However, the capacity of resources for the flexibility of given power system must be analyzed carefully as providing flexibility is rather expensive.
With the increasing penetration of renewable generations such as wind and solar energies to power systems, energy balance problem becomes harder to achieve, as a consequence of unpredictable and varying nature of renewable sources. Energy storage and demand side management schemes are gaining popularity over the years, which can be combined with renewable energy sources to increase flexibility of power systems.
## Wind Power on Power Systems
With the increasing environmental impacts of electricity production, renewable generation, such as wind and solar energies, has been penetrating to the power systems over the years. Today, 3.7% of global electricity is supplied by wind power and this percentage is expected to increase for the next years [1]. Total installed wind power capacity has reached approximately 487,000 MW at the end of 2016 and is expected to reach around 790,000 MW in 2020 [2]. Installed wind capacity over years can be observed in Figure X [3].
Figure X Historical development of global installed wind capacity
With the increasing penetration of wind energy to power systems, security and reliability of power systems are negatively affected, as a consequence of unpredictable and varying nature of wind. Power output of wind turbine is highly dependent on wind speed and can be expressed as follows:
P = {1} over {2} {ρ} rsub {air} {C} rsub {p} left (λ , β right ) π {r} ^ {2} {v} ^ {3} (X)
where:
Cp(λ,β)	power coefficient, a function of the tip speed ratio λ and the pitch angle β
r	blade length
v	wind velocity
As it can be observed from Equation X, even small variations of wind speed can cause large power fluctuations. In Figure X, fluctuations of power output for a wind farm in Turkey can be observed. Power level frequencies of the wind farm can also be seen in Figure X.
Figure X Generation of a wind farm annually
Figure X Generation levels of a wind farm annually
With the increasing penetration of wind power into power systems, complexity of operation and planning of the systems increases. To cope with unpredictable and variable nature of wind, more power system flexibility is needed for high wind power penetration. To maintain reliability and security of the systems, additional reserves are needed. Energy storage technologies and demand side management schemes can be used for this purpose.
## ENERGY STORAGE SYSTEMS (ESSs)
In a power system, energy demand must be supplied instantaneously to preserve stability and quality of the system. Stability and quality of a power system decreases as an imbalance between supply and demand occurs. Scheduling of power systems with varying net load profile decreases the overall efficiency because of the deviations from optimal generation spot.
With the increasing penetration of renewable energy to power systems, security and reliability issues must be handled carefully, because of unpredictable and inconsistent nature of renewable energy sources. To cope with this problem, ESSs can be used to smooth out variable power generation of renewable energy systems, which makes renewable sources more reliable.
With the help of ESSs, electrical energy can be stored when generation exceeds consumption and stored energy can be used later for compensating generation shortage when needed. By doing this, generation can be maintained at a constant level, which increases the overall efficiency of the system. These systems can also be used for balancing short-term power fluctuations.
Widely-used categorization of ESSs is according to the form of energy used; mechanical, electro-chemical, chemical, electrical and thermal. [4]⁠
- Mechanical
  - Pumped hydro
  - Compressed air
  - Flywheel
- Electro-chemical
  - Secondary batteries
  - Flow batteries
- Chemical
  - Hydrogen
- Electrical
  - Double-layer capacitor
  - Superconducting magnetic coil
- Thermal
  - Sensible heat
  - Latent heat
  - Thermo-chemical
General properties of ESSs can be described as follows:
- Capacity: maximum energy storage limit of the system
- Power: charge/discharge power limit of the system
- Efficiency: ratio of the energy provided by discharging the system to the energy needed to charge the system
- Storage period: duration of stored energy without discharging
- Charge/discharge time: time to charge/discharge the system
- Cost: the capital and operation costs of the system
While choosing the suitable ESSs for a given system, these given properties must be carefully analized. Capacity and power are two important parameters for these systems. Capacity rate can be determined by control and energy management procedures while power rate can be determined by the difference between supply and demand.
Battery Energy Storage Systems (BESSs)
BESSs can be used for compensation of intermittent power output of wind farms. By charging and dicharging BESSs, excess power above predefined threshold levels can be stored and delivered lately. By combining BESSs with wind power generation, throughput of the existing grid infrastructure can be improved. However, it is important to adapt control strategies for optimal use of BESSs, as large-scale utilization of BESSs is not a cost effective choice [5].
BESSs are connected to the system at the point of common coupling and power converters are used for charging/discharging operations of BESSs which is shown in Figure X.
Figure X
Description and Model
For the BESS model, following parameters are defined:
State of Charge (SOC): SOC of a battery is defined as available capacity of the battery expressed as a percentage of its rated capacity. SOC is an indication of how longer a battery can continue to perform before recharging is needed [6].
Depleting or overcharging a battery is not desired, so proper limitations (i.e., 30%-100%) should be defined for SOC of the battery.
Deep Discharge: With increasing depth of discharge (DOD), cycle life of a battery decreases and deep discharge can cause permanent damage over battery cells.
To protect the battery from a permanent damage and increase the battery cycle life, proper limitation should be set for maximum discharge rating of the battery [7].
For the BESS model, simplified battery model developed in [5] is used. This simplified model is developed by using third-order battery model developed in [8], [9]. Third-order battery model and simplified model are shown in Figure X and Figure X, respectively.
In the third order battery model, components are nonlinear and current dependent. In simplified model, parasitic branch is ignored and circuit parameters are considered as constant to obtain a linear model. In [5], accuracy of the simplified model is justified so for the simulations, this simplified model is used.
Figure X
Figure X
For the simulations and analysis, BESS controller is developed to control charging/discharging of BESS through converter so that wind power output is dispatched hourly. While doing so, the limitations mentioned above (SOC and discharge current) are observed and preserved.
SOC of the battery is measured from battery voltage at the end. SOC limits are selected as SOCLL = 0.3 and SOCUL = 1 so that battery energy level changes between 30% and 100%. Charging and discharging of BESS are computed considering net load, difference between wind generation and load demand.
Thermal Energy Storage (TES)
Introduction
TES technology is used for storing thermal energy by heating or cooling a storage medium, to be used for heating and cooling needs later. Buildings and industrial processes are the main sectors where TES units are used. With the utilization of TES units, electricity consumption of the buildings does not have to be instantenously with the heating or cooling demand, as heating or cooling demand can be supplied with stored energy, which can be applied to shift electricity consumption. With the effective control of TES units, electric load profile for building’s thermal needs can be rearranged without affecting total energy consumption or temperature comfort for the buildings.
Thermal energy can be stored in three ways, in the form of sensible heat, latent heat or thermo-chemical energy. In the form of sensible heat storage, thermal energy is stored by heating or cooling a liquid or solid storage medium. In the form of latent heat storage, phase change materials (PCMs) are used for storing thermal energy. Thermo-chemical storage (TCS) is based on chemical reactions to store and release thermal energy.
Sensible heat storage is based on the specific heat of a storage medium which limits the storage capacity of these systems. PCMs use latent heat of the phase change and stored energy can be much more higher compared to sensible heat storage. In TCS, thermo-chemical reactions are used to store thermal energy for heating and cooling applications and in these systems storage capacity can be much higher.
Performance of TES units depends on system application and needs. PCM and TCS systems are more expensive compared to sensible heat storage and are suitable for applications where high number of storage cycles are needed.

Description and Model
Chilled water is generated with chillers and cooling towers. Chillers are used for removing the heat from chilled water loop and cooling towers are used for rejecting the heat from chiller cycle to ambient environment.
Storage element is used for shifting cooling thermal energy load. Load shifting logic depends on several factors such as renewable energy penetration, ambient temperature, temperature comfort level.
Storage Model
Definitions for the storage model are,
capacity	stored energy
max_capacity	maximum energy level
power	charging or discharging power
max_power	maximum charging/discharging power
charging_efficiency	efficiency of charging cycle
discharging_efficiency	efficiency of discharging cycle
TES unit is used as a buffer, which can shift the electrical power consumption of the system when needed. TES unit can operate in two modes, charging and discharging. In charging mode, when the chillers’ output power is greater than the power need by buildings, the excess power is stored in TES unit. In discharging mode, when the chillers’ output power is less than the power need by buildings, TES unit compensates for the power difference.

Chiller
Definitions for the chiller model are,
max_power	maximum electrical power input of chiller
power_in	electrical power consumption of chiller
power_out	cooling power output of chiller
efficiency	efficiency of chiller
Chiller unit is used for supplying cooling power for TES unit and buildings depending on need of the system.
Building Model
A simplified model for temperature dynamics of a space can be created using a resistance-capacitance (RC) circuit analogy,
C dot T = u + P_{d} + ( T_{o} - T ) over R (1)
where
T	inside temperature
Pd	external disturbance load
To	outside temperature
u	heating and cooling power input
The simplified thermal mass model (1) can be used for energy conversion problems, considering entire building and average temperature of all building spaces.
For discrete time, equation (1) can be represented with a sampling time of Δt,
T(k+1) = A T(k) + B u(k) + d(k) (2)
where
A = 1- {Δt} over {R C} , B = {Δt} over {C} , d = {P_{d} Δt} over {C} + {T_{o} Δt} over {R C}
For the simplification of building model, Pd is ignored and equation (2) becomes,
T_{change} = {Δt} (u over C + {T_{o} - T} over RC) (3)
Control Algorithm
For the control of the system, some critical parameters are defined,
Tmin	minumum temperature level of building environment
Tmax	maximum temperature level of building environment
Pdiff	difference between power generation and consumption
Δt	control time step
# CHAPTER
SIMULATIONS AND RESULTS
In this thesis, power system computer-aided design (PSCAD)/ electromagnetic transients including dc (EMTDC) is used for the simulations.
Simulations
[1]	“WIND IN NUMBERS | GWEC.” [Online]. Available: http://www.gwec.net/global-figures/wind-in-numbers/. [Accessed: 11-May-2017].
[2]	“Cumulative-Market-Forecast-by-Region-2016-2020-1.jpg (2091×1123).” [Online]. Available: http://www.gwec.net/wp-content/uploads/2016/04/Cumulative-Market-Forecast-by-Region-2016-2020-1.jpg. [Accessed: 11-May-2017].
[3]	“full-text.”
[4]	K. Han and T. Carson, “Executive summary,” Management, vol. II, pp. 10–16, 2008.
[5]	S. Teleke, M. E. Baran, S. Member, S. Bhattacharya, and A. Q. Huang, “Optimal Control of Battery Energy Storage for Wind Farm Dispatching,” IEEE Trans. Energy Convers., vol. 25, no. 3, pp. 787–794, 2010.
[6]	“Battery State of Charge Determination.” [Online]. Available: http://www.mpoweruk.com/soc.htm. [Accessed: 12-May-2017].
[7]	“Battery Life and How To Improve It.” [Online]. Available: http://www.mpoweruk.com/life.htm. [Accessed: 12-May-2017].
[8]	M. Ceraolo, “New dynamical models of lead-acid batteries,” IEEE Trans. Power Syst., vol. 15, no. 4, pp. 1184–1190, 2000.
[9]	S. Barsali and M. Ceraolo, “Dynamical models of lead-acid batteries: implementation issues,” Energy Conversion, IEEE Trans., vol. 17, no. 1, pp. 16–23, 2002.