# CHAPTER 1
# INTRODUCTION
## Motivation for the Thesis
Energy supply is one of the main interests of today’s society and energy consumption is considered as an important parameter to determine the level of development of a society. World’s total energy consumption has been increasing throughout the years and expected to rise from 549 quadrillion Btu in 2012 to 815 quadrillion Btu in 2040, an increase of 48% [1]⁠.
Since the industrial revolution, fossil fuels are remained as the main source of energy. However, negative impacts of these sources led the search for alternative methods to fulfill energy requirements. Climate change, which is the result of increasing greenhouse gases in the atmosphere, is the main concern about fossil fuels. Moreover, fossil fuels are non-renewable energy sources, so there is a limited supply. Renewable energy generation has been growing rapidly, with wind power having the highest percentage. In 2015, the wind energy was the most popular renewable energy source with 3.7% of the global electricity supply and this percentage is expected to increase for the next years [2]⁠. Historical development of global installed wind energy capacity over the years can be observed in Fig. 1-1 [3]⁠. Annual installations of wind energy capacity have been in excess of 50 GW for the last three years and at the end of 2016, total installed wind power capacity has reached to 486.8 GW.

Fig. 1-1: Historical development of installed wind capacity globally [3]⁠
In Fig. 1-2 [3]⁠, market forecast of wind energy capacity is shown with the growth rate expectations. Cumulative capacity growth rate is expected to be over 10% for the next 5 years and total wind energy capacity is expected to reach around 817 GW in 2021.

Fig. 1-2: Market forecast of wind capacity [3]⁠
In a similar way to global development, wind energy capacity in Turkey also has been increasing over the years. Installed wind energy capacity over the years in Turkey can be observed in Fig. 1-3 [4]⁠. With 1,387 MW installation last year, total wind capacity of Turkey is brought to 6,106 MW, which was enough to supply 7.3% of electricity demand of the country in 2016. Considering limited oil and gas reserves, Turkish government has set a national target of total wind power capacity to 20 GW by 2023 [3]⁠.

Fig. 1-3: Historical development of installed wind capacity in Turkey [4]⁠
Relation of power output of a wind turbine to wind speed can be expressed as follows:
P=1over2 %rho_air A v^3 C_p	(1-1)
where:
P	power output (W)
%rho_air	air density (kg/m3)
A	swept area (m2)
v	wind speed (m/s)
C_p	power coefficients
As it can be observed from Eq. 1-1, power output of a wind turbine is highly dependent on wind speed and even small variations of wind speed can cause large fluctuations in power output. Due to intermittent nature of wind, high level penetration of wind energy brings uncertainty and variability into power systems and energy balance problem becomes harder to achieve.
In Fig. 1-4, 10 minutes interval power output measurements of a wind farm in Turkey is shown. Daily fluctuations of wind generation with steep rises and sudden drops can be recognized in this figure.

Fig. 1-4: Daily generation of a wind farm in Turkey
The impact of increasing wind power penetration level to stability and reliability of the power system can be summarized as follows [5]⁠:
Reliability problems: Net-load variations can be tracked by conventional generators at low level integration of wind power to the power system [6]⁠. However, increasing penetration of wind energy eventually affects the system reliability as wind power output fluctuations are not controllable and generally wind generation is not related to the demand pattern, which leads an increase on the difference between peak and off-peak periods. As a result, committed conventional generators cannot compensate the sudden and large changes of wind power output.
Stability Problems: Wind turbine generators cannot provide large contributions to frequency support, unlike synchronous generators [7]⁠. Wind power output fluctuations will also weaken voltage stability of the grid due to generation and load mismatch [8]⁠.
Considering expected share of wind generation in overall electric power generation to grow significantly over the years, more flexibility in power systems will be required to handle with the negative impacts of wind power. In the near future, system flexibility needs which has been driven by variable demand up to this day, will begin to be driven by supply variability.
For the integration of renewable energy into power system effectively, four main options are proposed to provide flexibility to the power systems [9]⁠:
- Dispatchable generation
- Transmission and distribution expansion
- Demand-side management
- Energy storage
## Aims of the Thesis
With the high level penetration of wind generation, power systems are affected negatively due to intermittent nature of wind. One of the effects of wind power integration over power systems is transmission and distribution (T&D) upgrade need over existing structures. Considering the high investment cost of upgrade, T&D upgrade deferral becomes very profitable in specific cases.
In Fig. 1-5, power output of a wind farm in Turkey is shown for one year period. Power levels of this wind farm is also provided in Fig. 1-6. As it can be observed from these figures, wind generation is highly variable with a high peak to average ratio. Considering a modest overload over T&D system, demand-side management and energy storage applications can be used for absorbing power above the capacity of T&D line or component and releasing the stored energy when the T&D capacity is suitable.

Fig. 1-5: Generation of a wind farm in Turkey over a year

Fig. 1-6: Generation levels of a wind farm in Turkey over a year
Energy storage systems (ESSs) and demand-side management (DSM) are two main methods that can be integrated into power systems to supply the additional flexibility. In this chapter, general background of the thesis is presented. Main characteristics and applications of ESSs and DSM are explained. T&D system upgrade deferral concept is also introduced at the end of this chapter.
In this thesis, demand-side management and energy storage applications are chosen for the T&D upgrade deferral applications. Economical analysis of T&D system upgrade deferral will be investigated in presence of wind generation.
## Outline of the Thesis
Outline of the thesis can be formed as follows:
- Chapter 2 explains the flexibility concept and gives a general idea of the impact of wind generation on power systems. Literature review on energy storage systems and demand-side management are also provided in this chapter.
- Chapter 3 presents the modeling of both energy storage and demand-side management elements. Approach of transmission line capacity is also introduced in this chapter.
- Chapter 4 illustrates the contribution of storage systems and demand-side management to economical aspects of transmission systems with the simulation results and evaluations.
- Chapter 5 concludes the study and possible future works on that subject are discussed.
# CHAPTER 2
# PROVIDING FLEXIBILITY INTO POWER SYSTEMS FOR WIND POWER INTEGRATION
## Introduction
The main concern about planning and operation of the power systems is maintaining the equilibrium between safety and efficiency. As the share of renewable energy over power systems increases, sustaining this equilibrium becomes a more complicated problem to be solved. In order to reduce the impacts of renewable generation on power systems, further flexibility is required.
Flexibility of a power system is defined as the ability of the power system to respond to changes in demand and supply over a range of operating conditions [10]⁠. All power systems contain some degree of flexibility, as variability and uncertainty are always an issue and systems are designed to match the supply and demand all the time. However, with the renewable generation integration into power systems, variability and uncertainty become a problem of generation-side, in addition to load-side.
For better understanding, the impact of wind generation on net-load can be observed in Fig. 2-1 [11]⁠. Here, net-load represents the demand which will be supplied by the conventional generators when the wind generation is utilized. It can be observed that wind generation leads to steeper ramps, deeper turn downs and shorter peaks on net-load, which affects the operations of conventional generators.

Fig. 2-1: Impact of wind generation on net-load [11]⁠
In conventional power systems, generators with fast start time, high ramp-up/down rates and low minimum up/down times are used to provide flexibility. However, considering the impacts of renewable generation on power systems, alternative methods are needed to compensate emerging effects. Energy storage systems (ESSs) and demand-side management (DSM) are two main methods that can be integrated into power systems to supply additional flexibility.
In this chapter, general background of the thesis is presented. Main characteristics and applications of ESSs and DSM are explained and evaluated for the wind power integration.
## Energy Storage Systems
In a power system, energy demand must be supplied instantaneously to preserve stability and quality of the system. In addition, scheduling of power systems with varying net-load profile decreases the overall efficiency because of the deviations from optimal generation spot.
Conventional power systems operate effectively without storage, but efficiency of the systems can be increased with the integration of ESSs. Additionally, ESSs can be used to reduce the effects of renewable generation integration and increase reliability and stability of the systems.
Considering the recent development and advances in energy storage technology, ESSs have become a suitable solution for the negative impacts of wind power integration. An ESS can be described in terms of the following properties [12]⁠:
Storage capacity (kWh) is the amount of energy that can be stored by the ESS.
Power rating (kW) is the rate of energy transfer per unit time which can be supplied or consumed by the ESS.
Energy to power ratio is the ratio of ESS storage capacity to its power rating. ESSs with higher energy to power ratio can deliver power for longer periods. ESS applications for different energy to power ratios are listed at Table 2.1 [12]⁠.
Table 2.1: ESS applications for different energy to power ratios [12]⁠
Seconds to minutes	Daily	Weekly to monthly
Primary/Secondary frequency control / Spinning reserve / Voltage control / Black start capability / Peak shaving / Island grids / Uninterruptible power supply	Tertiary frequency control / Standing reserve / Load leveling / Island grids / Residential storage systems / Uninterruptible power supply	Storage for “Dark calm” periods / Island grids

Energy density (kWh/m3) is the ratio of ESS storage capacity to its volume. ESSs with high energy density can be used for applications where the volume of storage system is limited.
Power density (kW/m3) is the ratio of ESS power rating to its volume. ESSs with high power density can be used for high power applications with short duration of power usage.
Specific energy (kWh/kg) is the ratio of ESS storage capacity to its weight. ESSs with high specific energy can be used for application with high energy demand and weight limitations.
Specific power (kW/kg) is the ratio of ESS power rating to its weight. ESSs with high specific power can be used for applications with high power demand and weight limitations.
Depth of Discharge (%) is the ratio of discharged energy to storage capacity of the ESS. For a fully discharged storage system, depth of discharge (DoD) is 100%.
State of Charge (%) is the ratio of remaining energy to usable storage capacity of the ESS. For a fully charged storage system, state of charge (SoC) is 100%.
Efficiency (%) is the ratio of output energy to input energy of ESS. With increasing losses, efficiency of the ESS decreases.
Self discharge (sec) is the energy loss of ESS due to internal processes at standby.
Start-up time (sec) is the time period between power request and first power delivery.
Ramp-up time (sec) is the time period required from zero to full power transition.
Ramp rate (kW/sec) is the ratio of maximum power to ramp-up time.
Deployment/response time (sec) is the time period between power request and full power delivery. In Fig. 2-2 [12]⁠, time parameters of an ESS can be observed.

Fig. 2-2: Response time of an ESS [12]⁠
Full cycle is the complete discharging and charging process of the ESS. Discharging the system to minimum energy limit and then charging it to maximum energy limit is regarded as one full cycle of an ESS.
Equivalent full cycle is the overall discharging and charging process with any DoD per cycle divided by available capacity. Discharging and charging the system 2 times with 50% DoD or 4 times with 25% DoD are both considered as one equivalent full cycle.
Cycle life is the number of full cycles that can be delivered by an ESS under specified conditions before the ESS cannot meet specified criteria.
Calendar life is the lifetime of an ESS when it is not used.
While choosing the suitable ESS for a given power system, these given properties must be carefully analyzed. Storage capacity and power rating are two important parameters for storage systems. Capacity rate can be determined by control and energy management procedures while power rate can be determined by the difference between supply and demand.
## Classification of ESSs
A widely-used classification of energy storage technologies is according to the form of energy used, as shown in Fig. 2-3 [5]⁠.

Fig. 2-3: Classification of energy storage technologies [5]⁠
ESSs can be also categorized according to duration and frequency of the power supply [12]⁠:
Short-term: Short-term ESSs are used for instant energy supply. This type of ESSs are used mainly in primary and secondary frequency control and reactive power compensation applications. This storage systems have low energy to power ratio of minutes and high charging and discharging rates. Generally, equivalent full cycles per day are very high for these systems.
Medium-term: Medium-term ESSs are used for matching the demand fluctuations between day and night. Energy to power ratio of this systems are typically several hours. These type of systems have typically one or two equivalent full cycles per day.
Long-term: Long-term ESSs are used for power supply during several days or weeks. These systems have very high energy to power ratio, and due to this high energy capacity and relatively low power, the number of equivalent full cycles per year is very few. This kind of systems can be used to overcome “dark calm” periods, when power generation shortage occurs in power systems with high renewable energy penetration.
Comparison of power rating and storage capacity of different energy storage technologies are shown in Fig. 2-4 [13]⁠. ESS applications with their definitions for generation support, transmission and distribution support and end-customer uses are listed at Table 2.2, Table 2.3 and Table 2.4 [14]⁠, respectively.

Fig. 2-4: Comparison of storage technologies [13]⁠
Table 2.2: Generation and system-level applications of ESSs [14]⁠
Application	Description
Wholesale Energy Services	Utility-scale storage systems for bidding into energy, capacity and ancillary services markets
Renewable Integration	Utility-scale storage systems providing renewable time shifting, load and ancillary services for grid integration
Stationary Storage for Transmission and Distribution Support	Storage systems for improving transmission and distribution system utilization factor, and transmission and distribution capital deferral

Table 2.3: Transmission and distribution system applications of ESSs [14]⁠
Application	Description
Transportable Storage for Transmission and Distribution Support	Transportable storage systems for transmission and distribution system support and transmission and distribution deferral at multiple sites as needed
Distributed Energy Storage Systems	Centrally managed modular systems providing increased customer reliability, grid transmission and distribution support and potentially ancillary services
Energy Services Company Aggregated Systems	Residential-customer-sited storage aggregated and centrally managed to provide distribution system benefits
Commercial and Industrial Power Quality and Reliability	Systems to provide power quality and reliability to commercial and industrial customers

Table 2.4: End-user applications of ESSs [14]⁠
Application	Description
Commercial and Industrial Energy Management	Systems to reduce time of use energy charges and demand charges for commercial and industrial customers
Home Energy Management	Systems to shift retail load to reduce time of use energy and demand changes
Home Backup	Systems for backup power for home offices with high reliability value

## Applications of ESSs
ESS applications for wind integration support can be categorized as generation-side, grid-side and demand-side applications [5]⁠:
Generation-side Applications
Different from conventional power plants, wind farm power output cannot be controlled in a strict way as a result of stochastic nature of wind. Power intermittency, ramp rates and limiting wind power output are the main challenges coming along with wind power integration into the power systems [15]⁠. Looking from the generation-side to overall system, controllability of a wind farm can be increased with the usage of ESSs.
  - Time shifting:
Wind power generation is a non-dispatchable source of electricity production and can only be forecasted with a limited certainty. The mismatch between wind power output with the demand pattern, e.g. high wind power generation during off-peak demand periods and vise versa, is a big challenge as the difference between peak and off-peak periods of the system net-load increases. Energy storage technologies can be used to match the wind power generation with load cycles by storing extra energy during high wind power generation and releasing it later during peak demand periods. In time shifting applications, huge amount of energy is required to be stored for long time periods, so it is important to consider storage capacity and energy to power ratio parameters of the ESSs in these applications.
  - Output smoothing:
Wind power generation can have sudden drops and steep rises as a result of variable wind speed. System stability will be affected with the sudden power output changes which will create frequency and voltage fluctuations. Power output of a wind farm can be smoothed out with energy storage technology applications, by storing excess energy during instantaneous increase in power generation and releasing the stored energy during sudden output power drops. Ramping capability of the ESSs is the most important parameter in these applications, as the storage system must response the fast changes of wind power output.
  - Transmission utilization efficiency:
Rich wind resources are often located in remote locations and transmission networks limitations becomes a serious problem to supply the energy demand, which is far from wind farm sites [16]⁠. With the usage of energy storage technology, efficiency of transmission utilization can be increased by reducing congestion over the network. Additionally, transmission and distribution upgrades can be deferred or in some cases avoided at all with proper usage of the ESSs.
Grid-side Applications
Increasing wind power generation reduces the stability and reliability of the grid, because of the intermittent nature of these supplies. Considering the distributed generation of wind farms over the system, net variability of the entire grid is lower compared to the integration of single wind power plant, so overall requirement of services is less than considering grid-side applications.
Energy storage technologies can be used to provide ancillary services to decrease the impact of wind power generation over system stability and reliability. Grid-side applications of the ESSs is listed according to response time of the systems at Table 2.5 [5]⁠.
Table 2.5 Grid-side applications of the ESSs [5]⁠
Response time	Application
Hours to days	Energy arbitrage / Load levelling
Minutes to hours	Reserves / Efficiency use of transmission network / Emergency power supplying / Black start
Seconds to minutes	Frequency regulation
Less than a second	Inertia emulation / Oscillation damping / Voltage support / Low Voltage Ride Through support

  - Energy arbitrage/load leveling:
In the electricity market, electricity prices vary during peak and off-peak hours. The variation of prices in Turkey in 2016 can be observed in Fig. 2-5 [17]⁠. Energy storage technologies can be used to reduce the gap between peak and off-peak prices, by storing low-cost energy during off-peak periods and releasing stored energy during peak periods with the higher price [18]⁠.

Fig. 2-5: Average of hourly electricity prices in Turkey [17]⁠
  - Frequency regulation:
ESSs can be used to provide frequency regulation to the wind farms by controlling active power output of storage with frequency deviation. Primary frequency control can be applied by using droop control in local systems. Active power output of the ESSs can be controlled according to frequency change on the grid [19]⁠. For secondary frequency control, an automatic control system can arrange the power outputs to response frequency deviations.
  - Inertia emulation:
The impact of sudden wind generation changes on frequency changes can be reduced by increasing inertia of grid. Apparent inertia of a grid can be increased with the integration of the ESSs, by controlling the active power output of the storage systems.
  - Oscillation damping:
Sudden power changes of wind farms can cause oscillations in an interconnected system which may led to synchronization loss of some machines [20]⁠. Energy storage technologies can be used to damp the system oscillations caused by variable wind generation output and increase the stability of the power system.
  - Voltage control support:
Voltage stability of the grid can decrease with the variable nature of wind generation output. Integration of energy storage technologies can increase reactive power support for voltage regulation by controlling converters connected to the grid [20]⁠.
  - Low Voltage Ride Through support:
Today, low voltage ride through (LVRT) capability of wind turbine generators are determined by grid codes. During severe grid faults, wind turbines should remain connected for reactive power support and in some situations maximum reactive power needs to be delivered by wind turbines [21]⁠. For such cases, energy storage technologies can support the power need by converters and control systems.
  - Reserve application:
For the stability and reliability of the system, emergency reserves are required as a result of forecast error of wind power output. Integration of energy storage technologies can be an option for the reserve applications.
  - Emergency power supply:
In the situation of a fatal failure, ESSs can be used to energize the power system from a shut-down condition [22]⁠.
  - Transmission utilization efficiency:
Integration of energy storage technologies into power systems can increase the efficiency of transmission network usage and transmission and distribution costs can be reduced by deferral of network upgrade.
Demand-side Applications
With the combination of ESSs and DSM, ancillary services can be provided for the grid using huge amount of variable loads as a virtual power plant (VPP).
## ESS Planning for Wind Power Integration Applications
Technical characteristics of an ESS, such as storage capacity, rating power and charging/discharging duration range can be determined by analyzing characteristics of a wind farm.
Fluctuations of wind generation output at different time scales is an important parameter for the ESS selection. While generation reserve and energy dispatch applications are related to low frequency fluctuations (minutes to hours), power system frequency control applications are related to high frequency applications (seconds to minutes) [23]⁠. High frequency fluctuations on the wind power output has an insignificant overall effect [24]⁠ and can be damped out by inertia of the turbine generator [25]⁠. As a result, it is required that energy to power ratio of the ESSs to be in the order of a few hours for wind integration support [5]⁠.
As the increasing rating capacity of wind farms is considered, large-scale energy storage technologies are required for wind integration applications. BESS, PHS and CAES technologies are suitable for the large-scale applications for their capability of storing energy for long periods at a high power rating. Among these three technologies, BESS is more suitable for the purpose, as PHS and CAES are limited by topographical constraints [26]⁠.
By taking account of the findings mentioned above and rapid development in battery technology and cost reduction, it is decided to study the BESS technology for the wind power applications. Two mainly used battery types in BESSs are lithium-ion and lead-acid batteries and their characteristics are summarized including future expectations at Table 2.6 and Table 2.7 [12]⁠, respectively.
Table 2.6 Characteristics of lithium-ion batteries [12]⁠
Lithium-ion batteries
Parameters	2013	2030 (Expected)
Round-trip efficiency	83-86 %	85-92 %
Energy density	200-350 Wh/l	250-550 Wh/l
Power density	100-3500 W/l	100-5000 W/l
Cycle life	1000-5000 full cycles	3000-10000 full cycles
Calender life	5-20 years (depending on temperature and SoC)	10-30 years (depending on temperature and SoC)
Depth of discharge	Up to 100 %	Up to 100 %
Self discharge	5 % per month	1 % per month
Power installation cost (converter)	150-200 €/kW	35-65 €/kW
Energy installation cost	300-800 €/kW	150-300 €/kW
Deployment time	3-5 ms
Site requirements	None
Main applications	Frequency control / Voltage control / Peak shaving / Load leveling / Electromobility / Residential storage systems

Table 2.7 Characteristics of lead-acid batteries [12]⁠
Lead-acid batteries
Parameters	2013	2030
Round-trip efficiency	75-80 %	78-85 %
Energy density	50-100 Wh/l	50-130 Wh/l
Power density	10-500 W/l	10-1000 W/l
Cycle life	500-2000 full cycles	1500-5000 full cycles
Calendar life	5-15 years (depending on temperature and SoC)	10-20 years (depending on temperature and SoC)
Depth of discharge	70 %	80 %
Self discharge	0.1-0.4 % per day	0.05-0.2 % per day
Power installation cost (converter)	150-200 €/kW	35-65 €/kW
Energy installation cost	100-250 €/kW	50-80 €/kW
Deployment time	3-5 ms
Site requirements	Ventilation due to gassing
Main applications	Frequency control / Peak shaving / Load leveling / Island grids / Residential storage systems / Uninterruptible power supply

## Demand-side Management
## In a conventional power system, the balance between generation and demand is maintained by controlling the power output of limited number of power plants. However, with the increasing penetration of renewable generation to the system, dispatch of generation capacity to provide the required services to follow the load profile becoming much more challenging. As an alternative way, controlling load-side to increase flexibility of the power system attracts increasing attention. With the help of global communication infrastructure and embedded systems, loads can be dispatched according to system needs [27]⁠.
With demand-side management (DSM), flexible loads can be scheduled considering the grid needs. If individual loads can be aggregated and controlled on command according to the requirement of power systems, the result will be the same as generation dispatch. For example, turning off a large number of loads when the demand exceeds generation will have the same effect of increasing generation or vice versa.
## Classification of DSM
DSM is defined as all the applications which can be applied to the demand-side of the power system. DSM can be categorized according to timing and impact of the applications on customer process, which can be observed in Fig. 2-6 [27]⁠.

Fig. 2-6: Categories of DSM [27]⁠
Energy Efficiency (EE): EE applications include increasing the efficiency of appliances and improvements on the system properties. Changing a refrigerator with a more efficient one or applying thermal insulation to a building are some examples that can be considered as EE applications. In addition, behavioral changes of users to increase efficiency of energy usage can be included in these applications.
Time of Use (ToU): In ToU tariffs, electricity prices change according to power consumption at that time. Electricity prices for third quarter of 2017 in Turkey for different consumers are tabulated at Table 2.8 [28]⁠. It can be seen that peak period electricity price are approximately 50% higher compared to day period price and 140% higher compared to night period price. Considering the big difference between electricity prices for different time periods of the day, customers are encouraged to arrange their power consumption to reduce the overall cost.
Table 2.8: Electric prices for different time periods in Turkey [28]⁠
	Day period (06:00-17:00)	Peak period (17:00-22:00)	Night period (22:00-06:00)
Industrial	28.9365 kr/kW	44.8500 kr/kW	17.4582 kr/kW
Commercial	33.3374 kr/kW	50.2713 kr/kW	21.1035 kr/kW
Residential	33.0447 kr/kW	49.9784 kr/kW	20.8112 kr/kW

Demand Response (DR): DR is defined as controlling flexible loads to shift power consumption from peak periods to off-peak periods. By doing so, energy consumption is not decreased but only shifted through time. However, by shifting peak power consumption through time, the overall efficiency of power system is increased. Impact of DR on power consumption can be observed in Fig. 2-7 [29]⁠.

Fig. 2-7: Impact of demand response on power consumption [29]⁠
Spinning Reserve (SR): Combination of large number of loads can be used for frequency regulation applications, namely primary and secondary frequency control. Primary frequency control is done by controlling active power, considering frequency changes over time. In secondary frequency control, frequency is restored with additional active power to the system. With SR applications, combination of large number of loads can be controlled like a virtual power plant with negative power output to the grid.
## Applications of DSM
DSM applications can be classified according to the time scale of the load control (from milliseconds to hours) [30]⁠:
Under a second: Frequency changes in a system can be observed and dispatchable loads can respond to these changes to maintain system security. Either loads can be shut down when a steep frequency drop occurs on the grid, or they can response to frequency changes according to frequency error, similar like droop control of conventional power plants. As wind power plants cannot participate to droop control, demand dispatch can be a solution for the intermittent wind power output.
Seconds to minute: The ancillary services for power system regulation is provided by power plants in today’s power systems. An alternative way for serving these services to the power system is DSM. By controlling high number of loads with fast response, regulation can be provided in an efficient way.
Hours: Dispatchable loads can be controlled to match highly varying wind generation profile for a wind farm or even for a region, depending on the limits of aggregated loads. Rapid changes in wind power generation can be followed by DSM control, as the flexible loads generally have a fast response time. With the introduction of DSM into the power systems, the required fast-response generation capacity will be reduced.
## DSM Planning for Wind Power Integration Applications
DSM takes advantage of controllable loads and support the grid considering changing needs, so in order to dispatch loads, some flexibility is needed in demand-side. Some suitable loads for DSM applications can be listed as follows [30]⁠:
- Dishwashers
- Washers and dryers
- Electric hot water heaters
- Heating, ventilation and air-conditioning (HVAC) systems
- Battery charges for consumer electronics
- Plug-in vehicles
Considering the large number of aggregated flexible loads, demand dispatch can be an important factor for the power systems applications. However, there are some constraints for the flexible loads, so important parameters must be defined for each individual load, such as minimum and maximum power limits, how much and when energy is needed and number of cycles for a given time period. The main objective of demand dispatch is to serve the grid needs by dispatching loads while considering these limitations. Suitable services for the power systems can be developed by considering power and energy limitations of flexible loads as well as their response characteristics.
HVAC systems are chosen to be controlled in simulations in this study, as they are responsible for a high percentage of energy usage in residential, commercial and industrial sectors. End-use energy consumption for residential and commercial sectors in 2016 with the expectations in 2040 can be observed in Fig. 2-8 [31]⁠. Considering the energy consumption share overall, HVAC systems, when aggregated, can participate in matching generation and load, as well as ancillary services to support grid with suitable control methods.

Fig. 2-8: End-use energy consumption for residential and commercial sectors [31]⁠
Thermal behavior of a HVAC unit can be seen in Fig. 2-9 [32]⁠.

Fig. 2-9: Thermal behavior of a HVAC unit [32]⁠
A HVAC can be described in terms of the following properties [33]⁠:
Coefficient of Performance (CoP) is the HVAC efficiency measured in cooling/heating output divided by electrical power input.
Energy Efficiency Ratio (EER) is the ratio of cooling/heating capacity of HVAC to electrical power input at full-load conditions.
## Conclusion

# CHAPTER 3
# TRANSMISSION AND DISTRIBUTION UPGRADE DEFERRAL
## Introduction
For the power systems, existing T&D structures become insufficient over time due to growing peak demand and as a result, upgrade of the present structures becomes inevitable. The main problem of upgrading an existing T&D structure is the high investment cost, which is highly variable due to various factors, such as installation requirements and location. However, T&D upgrade can be deferred in specific conditions by using suitable technologies. Viability of T&D upgrade deferral can be examined by checking some criteria over present systems [34]⁠:
- High T&D investment cost
- High peak-to-average demand ratio
- Modest projected overload
- Slow peak demand growth
- Uncertainty about timing and/or likelihood of block load additions
- T&D construction delays or construction resource constraints
- T&D upgrade competes with other important projects for capital
ESS and DSM can be used to deliver a portion of peak demand for delaying large T&D structure upgrades. In need of an upgrade over existing structure, T&D upgrade factor is defined as the ratio of load carrying capacity to be added to present T&D structure. Common upgrade factor values range from 0.25 to 0.50 or more [34]⁠. By using ESS and DSM, small capacity additions can be used to defer large large T&D equipment upgrades.
For a better understanding of the concept of T&D upgrade deferral, an example case is demonstrated in Fig. 3-1 [34]⁠. For this case, an existing distribution system with a rated load carrying capacity of 12 MW is expected to be overloaded in the next year, considering a 2% load growth rate per year. In order to avert overloading of the equipment, load carrying capacity of T&D structure is planned to be increased with an upgrade factor of 0.33, from 12 MW to 16 MW. Considering the modest overload over the structure, upgrade need of the present structure can be delayed for some time using proper solutions.

Fig. 3-1: Planned upgrade of a distribution system due to increasing peak demand [34]⁠
In this study, impact of ESSs and DSM on transmission-side upgrade delay is investigated. This chapter contains the introduction of the constructed scenario with modeling and approaches used for the analysis of different cases.
## Description of the Scenario
In this thesis, a hypothetical scenario is constructed where a wind farm connected to a near organized industrial zone through distribution lines and overall system is connected to the transmission-side as shown in Fig. 3-2. Transmission-side capacity is occupied by power flow from/to the grid (Pline), which is the difference between wind power generation (Pwg) and industrial load (Poiz).

Pwg

Poiz

Organized Industrial Zone

Grid
Wind Farm

Pline

Fig. 3-2: Drawing of the hypothetical system
10 minute interval data of wind power generation and organized industrial zone power consumption are used in this study. Real data are obtained from Monitoring and Forecasting System Development for Wind Generated Electrical Power in Turkey (RITM) and National Power Quality Project (MGKP) of The Scientific and Technological Research Council of Turkey, Marmara Research Center, Energy Institute (TUBITAK MAM EE). In order to use the available data, raw data are organized and processed using R, which is an open source software environment for data manipulation, calculation and graphical display.
Missing data are common problem for data analysis, and can have significant effect considering the overall study. Percentage and distribution of missing data are two important factors which needed to be taken account. Databases of aforementioned projects are examined in order to find suitable data considering percentage and distribution of missing values. Information about raw data used in this study is tabulated at Table 3.1. The percentage of missing values is 0.77% for wind power generation data, which is an acceptable value considering the distribution of missing data. Industrial power consumption data used in this study does not contain any missing value.
Table 3.1: Missing data information about datasets
	Wind power generation	Industrial power consumption
Missing data percentage	%0.77	%0
Maximum number of consecutive missing data	8	0

Summary of chosen wind generation and industrial consumption data is provided at Table 3.2 and Table 3.3, respectively. As the impact of wind generation over the system with available data cannot be observed because of the high power consumption of organized industrial zone with respect to wind power generation, the difference is compensated by dividing the industrial load data by 4.
Table 3.2: Summary of chosen wind generation data
Min.	1st Qu.	Median	Mean	3rd Qu.	Max.
-0.24 MW	2.78 MW	9.62 MW	13.2 MW	22.13 MW	40.83 MW

Table 3.3: Summary of chosen industrial consumption data
Min.	1st Qu.	Median	Mean	3rd Qu.	Max.
-0.39 MW	95.73 MW	115.45 MW	104.72 MW	126.09 MW	157.03 MW

Power generation of chosen wind farm in 2016 and histogram of generation levels by bin width of 2 MW are plotted in Fig. 3-3 and Fig. 3-4, respectively. Low percentage of high power generation levels can be observed from the histogram figure, which is an important factor for T&D upgrade deferral applications.

Fig. 3-3: Power generation of chosen wind farm in 2016

Fig. 3-4: Histogram of wind power generation
Power consumption of chosen organized industrial zone in 2016 and histogram of consumption levels by bin width of 2 MW are plotted in Fig. 3-5 and Fig. 3-6, respectively. Weekly pattern of power consumption can be seen easily over the year except the first week of July and second week of September, which are corresponding to holidays in Turkey, Ramadan and Sacrifice Feasts, respectively.

Fig. 3-5: Power consumption of chosen organized industrial zone in 2016

Fig. 3-6: Histogram of industrial power consumption
With the integration of chosen aforementioned wind generation and industrial consumption profiles, power flow on the transmission-side of the system and histogram of power flow levels are shown in Fig. 3-7 and Fig. 3-8, respectively. In these figures, positive power corresponds to excess power generation of wind farm which is supplied to the grid, and negative power corresponds to power demand from the grid where wind generation cannot supply the industrial load. Summary of the power flow is also tabulated at Table 3.4.

Fig. 3-7: Power flow on transmission-side as a result of chosen generation and load profiles

Fig. 3-8: Histogram of power flow on transmission-side
Table 3.4: Summary of power flow from/to grid
Min.	1st Qu.	Median	Mean	3rd Qu.	Max.
-37.44 MW	-25.53 MW	-15.12 MW	12.99 MW	-2.25 MW	35.60 MW

## Modeling and Approaches
Power flow on transmission-side
Keeping power flow on transmission-side within the limits of transmission structures is the main purpose for this study. Considering the limitations, power flow constraints can be expressed as:
-P_line^max <= P_wg^t + P_bess^t - P_oiz^t - P_hvac^t <= P_line^max	(3-1)
where:
P_line^max	maximum transmission line capacity (MW)
P_wg^t	wind power generation of wind farms at time t (MW)
P_oiz^t	power demand of organized industrial zones at time t (MW)
P_bess^t	BESS power output at time t (MW)
P_hvac^t	power demand of HVAC units at time t (MW)
BESS
BESS can operate in three different modes; discharging, charging and idle. In charging mode, batteries are charged with the power drawn from grid and BESS can be considered as a load. In discharging mode, the power is supplied to the grid with discharge of the batteries and BESS can be considered as a generation unit. In idle mode, batteries are neither charged nor discharged. Mode variables of BESS are tabulated at Table 3.5 and stated as an equation.
Table 3.5: Mode variables of BESS
Variable	Idle mode	Discharging mode	Charging mode
u_dsch^t	0	1	0
u_ch^t	0	0	1

u_dsch^t + u_ch^t <= 1
where:
u_dsch^t	discharging mode indicator of BESS at time t
u_ch^t	charging mode indicator of BESS at time t
## Energy
SoC of a battery is defined as available capacity of the battery expressed as a percentage of its rated capacity. SoC is an indication of how longer a battery can continue to perform before recharging is needed [35]. SoC of a BESS can be expressed as:
SoC^{t+1} = SoC^{t} + {[ P_ch^t - P_dsch^t ]{{%DELTA T} over {60}}} over { S_cap }	(3-2)
S_cap = (E2P) P_{bess,rt }	(3-3)
where:
SoC^t	state of charge of BESS at time t
P_ch^t	power supplied to the BESS at time t (MW)
P_dsch^t	power drawn from BESS at time t (MW)
S_cap	storage capacity of BESS (MWh)
E2P	energy to power ratio of BESS (hours)
P_{bess,rt}	rated power of BESS (MW)
%DELTA T	time period (minutes)
Depleting or overcharging a battery is not desired, so proper limitations (i.e., 30%-100%) should be defined for SoC of the battery. SoC constraints can be expressed as:
SoC^min <= SoC^t <= SoC^max
where:
SoC^min	minimum allowed state of charge of BESS
SoC^max	maximum allowed state of charge of BESS
## Power
Discharging efficiency of a BESS is defined as the ratio of power supplied to grid to rate of change in stored energy in BESS. Charging efficiency of a BESS is defined as the ratio of rate of change in stored energy in BESS to power drawn from grid. Considering these definitions, power output of BESS can be expressed as:
P_bess^t = P_dsch^t { %eta_dsch} - P_ch^t {1 over %eta_ch}
where:
P_bess^t	BESS power output at time t (MW)
P_dsch^t	power drawn from BESS at time t (MW)
P_ch^t	power supplied to the BESS at time t (MW)
%eta_dsch	discharging efficiency of BESS
%eta_ch	charging efficiency of BESS
Battery charging and discharging powers are limited by the physical and chemical characteristics of the BESS. Limitations of charging and discharging powers of BESS can be expressed as:
0 <= P_dsch^t <= P_{bess,rt} u_dsch^t
0 <= P_ch^t <= P_{bess,rt} u_ch^t
where:
P_{ bess,rt}	rated power of BESS (MW)
P_dsch^t	power drawn from BESS at time t (MW)
P_ch^t	power supplied to the BESS at time t (MW)
(u_dsch)^t	discharging mode indicator of BESS at time t
(u_ch)^t	charging mode indicator of BESS at time t
Cost Equations
Capital expenditure (CAPEX) of a BESS is related to storage capacity of the BESS. CAPEX annuity of a BESS can be expressed as follows:
(CAPEX annuity)_BESS = CAPEX_BESS {{ IR (IR + 1)^L } over { (IR + 1)^L - 1 }}
CAPEX_BESS = (Stg) S^cap
where:
IR	interest rate (%/year)
L	lifetime period of BESS (years)
Stg	capital cost of BESS ($/MWh)
S^cap	storage capacity of BESS (MWh)
annual(OPEX(BESS)) = sum from{t=1} to {T}( Dschg P_dsch^t + Chg P_ch ^t ) * { {%DELTA T} over 60 }
where:
T	time instances in one year period
Dschg	discharging cost of BESS ($/MWh)
Chg	charging cost of BESS ($/MWh)
P_dsch^t	power drawn from the BESS at time t (MW)
P_ch^t	power supplied to the BESS at time t (MW)
%DELTA T	time period (minutes)
## Modeling of HVAC units
## Operation Mode
HVAC units can operate in three modes; cooling, heating and idle. In cooling mode, HVAC unit draws power from the grid to extract heat from the room. In heating mode, HVAC unit draws power from the grid to release heat to the room. In idle mode, HVAC unit neither cool nor heat the room. Mode variables of HVAC unit are tabulated at Table 3.6 and stated as an equation.
Table 3.6: Mode variables of HVAC unit
Variable	Idle mode	Cooling mode	Heating mode
(ucl)it	0	1	0
(uht)it	0	0	1

(u_cl)_i^t + (u_ht)_i^t <= 1
where:
(u_cl)_i^t	cooling mode indicator of HVACi at time t
(u_ht)_i^t	heating mode indicator of HVACi at time t
## Power
HVACs draw power from the grid both for cooling and heating modes. Total power drawn from the grid by HVACs can be expressed as follows:
P_hvac^t = sum from i=1 to N [(P_{hvac,rt})_i ((u_cl)_i^t + (u_ht)_i^t)]
where:
P_hvac^t	power demand of HVAC units at time t (kW)
(P_{hvac,rt})_i	rated power of HVACi at time t (kW)
(u_cl)_i^t	cooling mode indicator of HVACi at time t
(u_ht)_i^t	heating mode indicator of HVACi at time t
CoP for cooling mode is defined as the ratio of the removed heat to electrical input power and CoP for heating mode is defined as the ratio of the delivered heat to electrical input power [36]⁠. Considering these definitions, thermal power output of HVACs can be expressed as:
(Q_cl)^t_i = (CoP_cl)_i (P_{hvac,rt})_i (u_cl)_i^t
(Q_ht)^t_i = (CoP_ht)_i (P_{hvac,rt})_i (u_ht)_i^t
(P_{hvac,rt})_i	rated power of HVACi at time t (kW)
(CoP_cl)_i	coefficient of performance of HVACi for cooling
(CoP_ht)_i	coefficient of performance of HVACi for heating
(Q_cl)_i^t	equivalent cooling rate of HVACi at time t (kW)
(Q_ht)_i^t	equivalent heating rate of HVACi at time t (kW)
(u_cl)_i^t	cooling mode indicator of HVACi at time t
(u_ht)_i^t	heating mode indicator of HVACi at time t
Temperature Constraints
For modeling the HVAC unit, a simplified model for temperature dynamics of a space can be created using a resistance-capacitance (RC) circuit analogy [37]⁠. The simplified thermal mass model can be used for energy conversion problems, considering entire building and average temperature of all building spaces. Considering these approach, temperature of a building can be expressed as follows:
(T_room)_i^{t+1} = (T_room)_i^{t} + ({(T_out)_i^{t} - (T_room)_i^{t-1}} over {R_i C_i} + {(Q_ht)_i^t - (Q_cl)_i^t} over {C_i}) %DELTA t
where:
(T_room)_i^t	temperature of buildingi at time t (Co)
(T_out)_i^t	temperature of ambienti at time t (Co)
R_i	equivalent thermal resistance of buildingi (Co/kW)
C_i	equivalent heat capacity of buildingi (kJ/Co)
(Q_cl)_i^t	equivalent cooling rate of HVACi at time t (kW)
(Q_ht)_i^t	equivalent heating rate of HVACi at time t (kW)
Building temperature is controlled by the HVAC units and these limitations can be expressed as follows:
(T_room)_i^min < (T_room)_i^t < (T_room)_i^max
where:
(T_room)_i^t	temperature of buildingi at time t (Co)
(T_room)_i^min	minimum allowed temperature of buildingi (Co)
(T_room)_i^max	maximum allowed temperature of buildingi (Co)

# CHAPTER 4
# SIMULATIONS AND RESULTS
## Introduction
Ambient Temperature
For this thesis, ambient temperature data is collected from U.S. Climate Reference Network (USCRN) [38]⁠, as there is no accessible weather datasets of Turkey for sub hourly periods. In order to simulate suitable ambient temperature conditions for HVAC operations, USCRN monthly temperature data for 2016 are compared with the monthly temperature data collected from Turkish State Meteorological Service (TSMS) [39]⁠ for an area in Turkish Aegean Region between 1929-2016.. Monthly data of average temperature with minimum and maximum temperature averages taken from TSMS and USCRN are tabulated at Table 4.1 and Table 4.2, and collected data are plotted in Fig. 4-1 and Fig. 4-2, respectively.
Table 4.1: Summary of monthly temperature data taken from TSMS [39]⁠
	Average Temperature	Average Low Temperature	Average High Temperature
January	6.7	3.0	10.8
February	7.9	3.6	12.6
March	10.6	5.2	16.1
April	15.2	8.8	21.3
May	20.4	13.2	27
June	25.3	17.4	32.1
July	28.0	20.3	34.9
August	27.6	20.2	34.9
September	23.3	16.0	30.6
October	17.8	11.6	24.3
November	12.2	7.4	17.5
December	8.2	4.5	12.5

Fig. 4-1: Temperature of an area chosen from TSMS for one year period
Table 4.2: Summary of monthly temperature data taken from USCRN [38]⁠
	Average Temperature	Average Low Temperature	Average High Temperature
January	6.4	3.2	10.2
February	10.5	4.7	17.9
March	10.9	5.7	16.8
April	14.9	8.1	22.5
May	17.7	10.8	25.5
June	23.5	15.2	32.4
July	26.2	16.6	36.1
August	26.2	16.6	37.1
September	22.6	13.8	32.6
October	14.1	9.3	19.9
November	9.6	5.7	15.4
December	5.2	0.6	11.2

Fig. 4-2: Temperature of an area chosen from USCRN for one year period

Operation Mode of HVACs over a year
HVACs can operate in cooling or heating mode, depending on the ambient temperature. In order to determine operation mode of HVACs throughout the year, temperature data is divided into 12-hour periods.
By taking account the sunrise and sundown times throughout the year, days are separated into two equal periods; namely day period, between 07:00 to 19:00 and night period, between 19:00 to 07:00. In order to forecast the temperature of next period and determine the operation mode of HVACs accordingly, simple exponential smoothing method (SES) is used.
({hat T}_{amb})^{t+1} = %alpha (T_amb)^{t} + %alpha (1-%alpha) (T_amb)^{t-1} + %alpha (1-%alpha)^2 (T_amb)^{t-2} +...
where:
({hat T}_{amb})^{t+1}	ambient temperature forecast for time t+1
(T_amb)^t	ambient temperature at time t
%alpha	smoothing parameter
Average temperature for next HVAC operation period is forecasted using the average temperatures of last 14 HVAC operation periods (one week). Smoothing parameter is chosen as 0.7 and SES algorithm is done accordingly.
## Case 1
## Analysis of T&D Upgrade
Transmission-side capacity for this system is chosen as 35 MW. Maximum power flow to the grids in the current year is 34.08 MW, 2.63% below the transmission-side capacity.
In order to analyze T&D upgrade deferral, different wind generation capacity installations to the existing wind farm are considered. Industrial demand growth is determined as 2% per year, for all scenarios.
With the defined parameters, annual cost of transmission-side is calculated as $1,203,125.
## BESS Integration
For transmission-side upgrade deferral, BESS integration to the wind farm at the common coupling point is considered, which is shown in Fig. 4-3.

Fig. 4-3: System network with BESS integration

Grid

Pwind

Pgrid
Pload

Organized Industrial Zone

Wind Farm

BESS

Pbess

Energy to power ratio of the BESS is chosen as 2 hours. Initial state of charge (SoC) of the BESS is defined as 0.9 and limited between 0.3 and 0.9.
Wind Power Increase of 4%
Necessary BESS storage capacity for this scenario is calculated as 1.2 MWh. Power flow from/to the grid before and after BESS integration to the wind farm is shown in Fig. 4-4. Power output and SoC of the BESS are also shown in Fig. 4-5 and Fig. 4-6, respectively. Technical specifications and annual cost of the BESS for this scenario is tabulated at Table 4.3.

Fig. 4-4: Power flow of transmission-side (%4 wind power generation increase)

Fig. 4-5: Power output of BESS (%4 wind power generation increase)

Fig. 4-6: SoC of BESS (%4 wind power generation increase)
Table 4.3: BESS results (%4 wind power generation increase)
Power rating (MW)	Storage Capacity (MWh)	Annual cost ($)
0.6	1.2	60,000.21

Wind Power Increase of 6%
Necessary BESS storage capacity for this scenario is calculated as 2.6 MWh. Power flow from/to the grid before and after BESS integration to the wind farm is shown in Fig. 4-7. Power output and SoC of the BESS are also shown in Fig. 4-8 and Fig. 4-9, respectively. Technical specifications and annual cost of the BESS for this scenario is tabulated at Table 4.4.

Fig. 4-7: Power flow of transmission-side (%6 wind power generation increase)

Fig. 4-8: Power output of BESS (%6 wind power generation increase)

Fig. 4-9: SoC of BESS (%6 wind power generation increase)
Table 4.4: BESS results (%6 wind power generation increase)
Power rating (MW)	Storage Capacity (MWh)	Annual cost ($)
1.3	2.6	130,001.5

Wind Power Increase of 8%
Necessary BESS storage capacity for this scenario is calculated as 10.8 MWh. Power flow from/to the grid before and after BESS integration to the wind farm is shown in Fig. 4-10. Power output and SoC of the BESS are also shown in Fig. 4-11 and Fig. 4-12, respectively. Technical specifications and annual cost of the BESS for this scenario is tabulated at Table 4.5.

Fig. 4-10: Power flow of transmission-side (%8 wind power generation increase)

Fig. 4-11: Power output of BESS (%8 wind power generation increase)

Fig. 4-12: SoC of BESS (%8 wind power generation increase)
Table 4.5: BESS results (%8 wind power generation increase)
Power rating (MW)	Storage Capacity (MWh)	Annual cost ($)
5.6	11.2	560,005.8

Wind Power Increase of 10%
Necessary BESS storage capacity for this scenario is calculated as 22 MWh. Power flow from/to the grid before and after BESS integration to the wind farm is shown in Fig. 4-13. Power output and SoC of the BESS are also shown in Fig. 4-14 and Fig. 4-15, respectively. Technical specifications and annual cost of the BESS for this scenario is tabulated at Table 4.6.

Fig. 4-13: Power flow of transmission-side (%10 wind power generation increase)

Fig. 4-14: Power output of BESS (%10 wind power generation increase)

Fig. 4-15: SoC of BESS (%10 wind power generation increase)
Table 4.6: BESS results (%10 wind power generation increase)
Power rating (MW)	Storage Capacity (MWh)	Annual cost ($)
11.6	23.2	1,160,014

# CHAPTER 5
# CONCLUSION
REFERENCES

[1]	U.S. Energy Information Administration, International Energy Outlook 2016, vol. 0484(2016), no. May 2016. 2016.
[2]	“WIND IN NUMBERS | GWEC.” [Online]. Available: http://www.gwec.net/global-figures/wind-in-numbers/. [Accessed: 11-May-2017].
[3]	GWEC, “Global Wind Report 2016,” p. 76, 2017.
[4]	Turkish Wind Energy Association, “Türkiye Rüzgar Enerjisi İstatistik Raporu,” 2017.
[5]	H. Zhao, Q. Wu, S. Hu, H. Xu, and C. N. Rasmussen, “Review of energy storage system for wind power integration support,” Appl. Energy, vol. 137, pp. 545–553, 2015.
[6]	K. Dvijotham, S. Backhaus, and M. Chertkov, “Operations-Based Planning for Placement and Sizing of Energy Storage in a Grid With a High Penetration of Renewables,” vol. 98195, 2011.
[7]	Y. Sun, Z. Zhang, G. Li, and J. Lin, “Review on frequency control of power systems with wind power penetration,” Power Syst. Technol. ( …, pp. 1–8, 2010.
[8]	H. T. Le, S. Santoso, and T. Q. Nguyen, “Augmenting wind power penetration and grid voltage stability limits using ESS: Application design, sizing, and a case study,” IEEE Trans. Power Syst., vol. 27, no. 1, pp. 161–171, 2012.
[9]	“Commercialisation of Energy Storage in Europe,” 2015.
[10]	J. Cochran et al., “Flexibility in 21st Century Power Systems,” 21st Century Power Partnersh., vol. May, p. 14, 2014.
[11]	M. Milligan and NREL, “Capacity Value of Wind Plants and Overview of U.S. Experience,” 2011.
[12]	G. Fuchs, B. Lunz, M. Leuthold, and D. U. Sauer, “Technology Overview on Electricity Storage,” Inst. Power Electron. Electr. Drives (ISEA), RWTH Aachen Univ., no. June, p. 66, 2012.
[13]	IEC, “Electrical Energy Storage - White Paper,” Int. Electrotech. Comm., 2011.
[14]	“Electric Energy Storage Technology Options: A White Paper Primer on Applications, Costs, and Benefits,” 2010.
[15]	S. Teleke, M. E. Baran, S. Member, S. Bhattacharya, and A. Q. Huang, “Optimal Control of Battery Energy Storage for Wind Farm Dispatching,” IEEE Trans. Energy Convers., vol. 25, no. 3, pp. 787–794, 2010.
[16]	“Advantages and Challenges of Wind Energy | Department of Energy.” [Online]. Available: https://energy.gov/eere/wind/advantages-and-challenges-wind-energy. [Accessed: 08-Jun-2017].
[17]	“Elektrik Piyasası Özet Bilgiler Raporu,” 2016.
[18]	G. Celli, S. Mocci, F. Pilo, and M. Loddo, “Optimal integration of energy storage in distribution networks,” in 2009 IEEE Bucharest PowerTech: Innovative Ideas Toward the Electrical Grid of the Future, 2009.
[19]	J. Morren, S. Member, S. W. H. De Haan, W. L. Kling, and J. A. Ferreira, “Wind Turbines Emulating Inertia and Supporting Primary Frequency Control,” vol. 21, no. 1, pp. 2005–2006, 2006.
[20]	M. Swierczynski, R. Teodorescu, C. N. Rasmussen, P. Rodriguez, and H. Vikelgaard, “Overview of the energy storage systems for wind power integration enhancement,” 2010 IEEE Int. Symp. Ind. Electron., pp. 3749–3756, 2010.
[21]	D. D. Banham-Hall, G. A. Taylor, C. A. Smith, and M. R. Irving, “Flow batteries for enhancing wind power integration,” IEEE Trans. Power Syst., vol. 27, no. 3, pp. 1690–1697, 2012.
[22]	I. Gyuk, S. Eckroad, and T. Key, “EPRI-DOE handbook supplement of energy storage for grid connected wind generation applications,” EPRI-DOE Rep., 2004.
[23]	T. Zhang, Z. J. Bao, G. Chen, Q. Yang, and W. J. Yan, “Control strategy for a hybrid energy storage system to mitigate wind power fluctuations,” 2013 6th Int. Conf. Adv. Comput. Intell. ICACI 2013 - Proc., vol. 28, no. 1, pp. 27–32, 2013.
[24]	H. Chen, T. N. Cong, W. Yang, C. Tan, Y. Li, and Y. Ding, “Progress in electrical energy storage system: A critical review,” Prog. Nat. Sci., vol. 19, no. 3, pp. 291–312, 2009.
[25]	W. Li, G. Joós, and C. Abbey, “Wind power impact on system frequency deviation and an ESS based power filtering algorithm solution,” 2006 IEEE PES Power Syst. Conf. Expo. PSCE 2006 - Proc., vol. 2, pp. 2077–2084, 2006.
[26]	D. L. Yao, S. S. Choi, K. J. Tseng, and T. T. Lie, “Determination of short-term power dispatch schedule for a wind farm incorporated with dual-battery energy storage scheme,” IEEE Trans. Sustain. Energy, vol. 3, no. 1, pp. 74–84, 2012.
[27]	P. Palensky and D. Dietrich, “Demand side management: Demand response, intelligent energy systems, and smart loads,” IEEE Trans. Ind. Informatics, vol. 7, no. 3, pp. 381–388, 2011.
[28]	“EPDK (Enerji Piyasası Düzenleme Kurumu).” [Online]. Available: http://www.epdk.org.tr/TR/Dokumanlar/TDB/Elektrik. [Accessed: 02-Aug-2017].
[29]	S. van Renssen, “People power to the rescue,” Nat. Clim. Chang., vol. 4, no. 6, pp. 417–419, Jun. 2014.
[30]	A. Brooks, E. Lu, D. Reicher, C. Spirakis, and B. Weihl, “Demand dispatch,” IEEE Power Energy Mag., vol. 8, no. 3, pp. 20–29, 2010.
[31]	“Annual Energy Outlook,” 2017.
[32]	N. Lu, “An evaluation of the HVAC load potential for providing load balancing service,” IEEE Trans. Smart Grid, vol. 3, no. 3, pp. 1263–1270, 2012.
[33]	P. Test, “9 . ENERGY PERFORMANCE ASSESSMENT OF HVAC SYSTEMS,” pp. 115–121.
[34]	J. Eyer, “Electric Utility Transmission and Distribution Upgrade Deferral Benefits from Modular Electricity Storage,” 2009.
[35]	“Battery State of Charge Determination.” [Online]. Available: http://www.mpoweruk.com/soc.htm. [Accessed: 12-May-2017].
[36]	“Cooling Load - Convert kW/ton to COP or EER.” [Online]. Available: http://www.engineeringtoolbox.com/cop-eer-d_409.html. [Accessed: 23-Jul-2017].
[37]	Y. Ma, A. Kelman, A. Daly, and F. Borrelli, “Predictive Control for Energy Efficient Buildings with Thermal Storage: Modeling, Stimulation, and Experiments,” IEEE Control Syst., vol. 32, no. 1, pp. 44–64, 2012.
[38]	H. J. Diamond et al., “U.S. climate reference network after one decade of operations status and assessment,” Bull. Am. Meteorol. Soc., vol. 94, no. 4, pp. 485–498, 2013.
[39]	“Meteoroloji Genel Müdürlüğü.” [Online]. Available: https://mgm.gov.tr/veridegerlendirme/il-ve-ilceler-istatistik.aspx. [Accessed: 31-Jul-2017].