# CHAPTER 1
# INTRODUCTION
## Motivation for the Thesis
Energy supply is one of the main interests of today’s society and energy consumption is considered as an important parameter to determine the level of development of a society. World’s total energy consumption has been increasing throughout the years and expected to rise from 549 quadrillion Btu in 2012 to 815 quadrillion Btu in 2040, an increase of 48% [1]⁠.
Since the industrial revolution, fossil fuels are remained as the main source of energy. However, negative impacts of these sources led the search for alternative methods to fulfill energy requirements. Climate change, which is the result of increasing greenhouse gases in the atmosphere, is the main concern about fossil fuels. Moreover, fossil fuels are non-renewable energy sources, so there is a limited supply.
Renewable energy generation has been growing rapidly, with wind power having the highest percentage. In 2015, the wind energy was the most popular renewable energy source with 3.7% of the global electricity supply and this percentage is expected to increase for the next years [2]⁠. Annual installations of wind energy capacity have been in excess of 50 GW for the last three years and at the end of 2016, total installed wind power capacity has reached to 486.8 GW. Historical development of global installed wind energy capacity over the years can be observed in Fig. 1-1 [3]⁠.

Fig. 1-1: Historical development of installed wind energy capacity globally [3]⁠
In Fig. 1-2 [3]⁠, market forecast of wind energy capacity is shown with the growth rate expectations. Cumulative capacity growth rate is expected to be over 10% for the next 5 years and total wind energy capacity is expected to reach around 817 GW in 2021.

Fig. 1-2: Market forecast of wind energy capacity [3]⁠
In a similar way to global development, wind energy capacity in Turkey also has been increasing over the years. Installed wind energy capacity over the years in Turkey can be observed in Fig. 1-3 [4]⁠. With 1,387 MW installation in 2016, total wind capacity of Turkey is brought to 6,106 MW, which was enough to supply 7.3% of electricity demand of the country for the same year. Considering limited oil and gas reserves, Turkish government has set a national target of total wind power capacity to 20 GW by 2023 [3]⁠.

Fig. 1-3: Historical development of installed wind energy capacity in Turkey [4]⁠
Relation of power output of a wind turbine to wind speed can be expressed as follows:
P=1over2 %rho_air A v^3 C_p	(1-1)
where:
P	power output (W)
%rho_air	air density (kg/m3)
A	swept area (m2)
v	wind speed (m/sec)
C_p	power coefficient
As it can be observed from Eq. 1-1, power output of a wind turbine is proportional to the cube of the wind speed, so even small variations of the wind speed can cause large fluctuations in the power output. Power curve of ENERCON’s 2,300 kW rated power E-70 wind turbine generator is shown in Fig. 1-4 [5]⁠. Rapid change of the wind turbine generator power output with changing wind speed can be also observed from this figure.

Fig. 1-4: Power curve of ENERCON E-70 [5]⁠
In Fig. 1-5, 10 minutes interval power output measurements of a wind farm in Turkey is shown. In this figure, daily fluctuations of the wind generation due to variable wind speed throughout the day can be also recognized.

Fig. 1-5: Daily generation of a wind farm in Turkey
Due to intermittent nature of the wind, high level penetration of wind energy brings uncertainty and variability into power systems and energy balance problem becomes harder to achieve. The impact of increasing wind power penetration level to stability and reliability of the power system can be summarized as follows:
Reliability problems: Net-load variations can be tracked by conventional generators at low level integration of wind power to the power system. However, increasing penetration of wind energy eventually affects the system reliability as wind power output fluctuations are not controllable and generally wind generation is not related to the demand pattern, which leads an increase on the difference between peak and off-peak periods. As a result, committed conventional generators cannot compensate the sudden and large changes of wind power output.
Stability Problems: Synchronous generators can automatically regulate the speed governors to support frequency control. However, wind turbine generators can only provide small contributions to primary frequency support by using wind turbine level control; inertial control, droop control and deloading control [6]⁠. Wind power output fluctuations will also weaken voltage stability of the grid due to generation and load mismatch [7]⁠.
Considering expected share of wind generation in overall electric power generation to grow significantly over the years, more flexibility in power systems will be required to handle with the negative impacts of wind power. In the near future, system flexibility needs which has been driven by variable demand up to this day, will begin to be driven by supply variability.
For the integration of renewable energy into power system effectively, four main options are proposed to provide flexibility to the power systems [8]⁠:
- Dispatchable generation
- Transmission and distribution expansion
- Demand-side management
- Energy storage
## Aims of the Thesis
With the high level penetration of wind generation, power systems are affected negatively due to intermittent nature of the wind. One of the effects of wind power integration over power systems is transmission and distribution (T&D) upgrade need over existing structures. Considering the high investment cost of upgrade, T&D upgrade deferral becomes very profitable in specific cases by increasing flexibility to the power system. Energy storage systems (ESSs) and demand-side management (DSM) are two main methods that can be integrated into power systems to supply the additional flexibility.

Fig. 1-6: Generation of a wind farm in Turkey over a year

Fig. 1-7: Generation levels of a wind farm in Turkey over a year
In Fig. 1-6, power output of a wind farm in Turkey is shown for one year period. Power levels of this wind farm is also provided in Fig. 1-7. As it can be observed from these figures, wind generation is highly variable with a high peak to average ratio. Considering a modest overload over T&D system, ESS and DSM can be used for preventing the overload of the structures by using suitable control methods. The purpose of this study is to investigate the effects of ESS and DSM for the T&D upgrade deferral applications.
## Outline of the Thesis
Outline of the thesis can be formed as follows:
- Chapter 2 explains the flexibility concept and gives a general idea of the impact of wind generation on power systems. Literature review on energy storage systems and demand-side management are also provided in this chapter.
- Chapter 3 introduces transmission and distribution upgrade deferral concept. Explanation of the constructed scenario with the modeling of energy storage and demand-side management elements are also given in this chapter.
- Chapter 4 illustrates the contribution of storage systems and demand-side management to economical aspects of transmission systems with the simulation results and evaluations.
- Chapter 5 concludes the study and possible future works on that subject are discussed.

# CHAPTER 2
# PROVIDING FLEXIBILITY INTO POWER SYSTEMS FOR WIND POWER INTEGRATION
## Introduction
The main concern about planning and operation of the power systems is maintaining the equilibrium between safety and efficiency. As the share of renewable energy over power systems increases, sustaining this equilibrium becomes a more complicated problem to be solved. In order to reduce the impacts of renewable generation on power systems, further flexibility is required.
Flexibility of a power system is defined as the ability of the power system to respond to changes in demand and supply over a range of operating conditions [9]⁠. All power systems contain some degree of flexibility, as variability and uncertainty are always an issue and systems are designed to match the supply and demand all the time. However, with the renewable generation integration into power systems, variability and uncertainty become a problem of generation-side, in addition to load-side.
For better understanding, the impact of wind generation on net-load can be observed in Fig. 2-1 [9]⁠. Here, net-load represents the demand which will be supplied by the conventional generators when the wind generation is utilized. It can be observed that wind generation leads to steeper ramps, deeper turn downs and shorter peaks on net-load, which affects the operations of conventional generators.

Fig. 2-1: Impact of wind generation on net-load [9]⁠
In conventional power systems, generators with fast start time, high ramp-up/down rates and low minimum up/down times are used to provide flexibility. However, considering the impacts of renewable generation on power systems, alternative methods are needed to compensate emerging effects. Energy storage systems (ESSs) and demand-side management (DSM) are two main methods that can be integrated into power systems to supply additional flexibility.
In this chapter, general background of the thesis is presented. Main characteristics and applications of ESSs and DSM are explained and evaluated for the wind power integration.
## Energy Storage Systems
In a power system, energy demand must be supplied instantaneously to preserve stability and quality of the system. In addition, scheduling of power systems with varying net-load profile decreases the overall efficiency because of the deviations from optimal generation spot.
Conventional power systems operate effectively without storage, but efficiency of the systems can be increased with the integration of ESSs. Additionally, ESSs can be used to reduce the effects of renewable generation integration and increase reliability and stability of the systems.
Considering the recent development and advances in energy storage technology, ESSs have become a suitable solution for the negative impacts of wind power integration. An ESS can be described in terms of the following properties [10]⁠:
Storage capacity (kWh) is the amount of energy that can be stored by the ESS.
Power rating (kW) is the rate of energy transfer per unit time which can be supplied or consumed by the ESS.
Energy to power ratio is the ratio of ESS storage capacity to its power rating. ESSs with higher energy to power ratio can deliver power for longer periods. ESS applications for different energy to power ratios are listed at Table 2.1 [10]⁠.
Table 2.1: ESS applications for different energy to power ratios [10]⁠
Seconds to minutes	Daily	Weekly to monthly
Primary/Secondary frequency control / Spinning reserve / Voltage control / Black start capability / Peak shaving / Island grids / Uninterruptible power supply	Tertiary frequency control / Standing reserve / Load leveling / Island grids / Residential storage systems / Uninterruptible power supply	Storage for “Dark calm” periods / Island grids

Energy density (kWh/m3) is the ratio of ESS storage capacity to its volume. ESSs with high energy density can be used for applications where the volume of storage system is limited.
Power density (kW/m3) is the ratio of ESS power rating to its volume. ESSs with high power density can be used for high power applications with short duration of power usage.
Specific energy (kWh/kg) is the ratio of ESS storage capacity to its weight. ESSs with high specific energy can be used for application with high energy demand and weight limitations.
Specific power (kW/kg) is the ratio of ESS power rating to its weight. ESSs with high specific power can be used for applications with high power demand and weight limitations.
Depth of discharge is the ratio of discharged energy to storage capacity of the ESS. For a fully discharged storage system, depth of discharge (DoD) is 100%.
State of charge is the ratio of remaining energy to usable storage capacity of the ESS. For a fully charged storage system, state of charge (SoC) is 100%.
Efficiency is the ratio of output energy to input energy of ESS. With increasing losses, efficiency of the ESS decreases.
Self discharge (sec) is the energy loss of ESS due to internal processes at standby.
Start-up time (sec) is the time period between power request and first power delivery.
Ramp-up time (sec) is the time period required from zero to full power transition.
Ramp rate (kW/sec) is the ratio of maximum power to ramp-up time.
Deployment/response time (sec) is the time period between power request and full power delivery. In Fig. 2-2 [10]⁠, time parameters of an ESS can be observed.

Fig. 2-2: Response time of an ESS [10]⁠
Full cycle is the complete discharging and charging process of the ESS. Discharging the system to minimum energy limit and then charging it to maximum energy limit is regarded as one full cycle of the ESS.
Equivalent full cycle is the overall discharging and charging process with any DoD per cycle divided by available capacity. Discharging and charging the system 2 times with 50% DoD or 4 times with 25% DoD are both considered as one equivalent full cycle.
Cycle life is the number of full cycles that can be delivered by the ESS under specified conditions before the ESS cannot meet specified criteria.
Calendar life is the lifetime of the ESS when it is not used.
While choosing the suitable ESS for a given power system, these given properties must be carefully analyzed. Storage capacity and power rating are two important parameters for storage systems. Capacity rate can be determined by control and energy management procedures while power rate can be determined by the difference between supply and demand.
## Classification of ESSs
A widely-used classification of energy storage technologies is according to the form of energy used; mechanical, electrochemical, chemical, electromagnetic and thermal. Examples of energy storage technologies according to stored energy form can be observed in Fig. 2-3 [11]⁠.

Fig. 2-3: Classification of energy storage technologies [11]⁠
ESSs can be also categorized according to duration and frequency of the power supply [10]⁠:
Short-term ESSs: Short term ESSs are used for instant energy supply. This type of ESSs are used mainly in primary and secondary frequency control and reactive power compensation applications. This storage systems have low energy to power ratio of minutes and high charging and discharging rates. Generally, equivalent full cycles per day are very high for these systems.
Medium-term ESSs: Medium-term ESSs are used for matching the demand fluctuations between day and night. Energy to power ratio of this systems are typically several hours. These type of systems have typically one or two equivalent full cycles per day.
Long-term ESSs: Long-term ESSs are used for power supply during several days or weeks. These systems have very high energy to power ratio, and due to this high energy capacity and relatively low power, the number of equivalent full cycles per year is very few. This kind of systems can be used to overcome “dark calm” periods, when power generation shortage occurs in power systems with high renewable energy penetration.
Comparison of power rating and storage capacity of different energy storage technologies are shown in Fig. 2-4 [12]⁠. ESS applications with their definitions for generation support, transmission and distribution support and end-customer uses are listed at Table 2.2, Table 2.3 and Table 2.4 [13]⁠, respectively.

Fig. 2-4: Comparison of storage technologies [12]⁠
Table 2.2: Generation and system-level applications of ESSs [13]⁠
Application	Description
Wholesale Energy Services	Utility-scale storage systems for bidding into energy, capacity and ancillary services markets
Renewable Integration	Utility-scale storage systems providing renewable time shifting, load and ancillary services for grid integration
Stationary Storage for Transmission and Distribution Support	Storage systems for improving transmission and distribution system utilization factor, and transmission and distribution capital deferral

Table 2.3: Transmission and distribution system applications of ESSs [13]⁠
Application	Description
Transportable Storage for Transmission and Distribution Support	Transportable storage systems for transmission and distribution system support and transmission and distribution deferral at multiple sites as needed
Distributed Energy Storage Systems	Centrally managed modular systems providing increased customer reliability, grid transmission and distribution support and potentially ancillary services
Energy Services Company Aggregated Systems	Residential-customer-sited storage aggregated and centrally managed to provide distribution system benefits
Commercial and Industrial Power Quality and Reliability	Systems to provide power quality and reliability to commercial and industrial customers

Table 2.4: End-user applications of ESSs [13]⁠
Application	Description
Commercial and Industrial Energy Management	Systems to reduce time of use energy charges and demand charges for commercial and industrial customers
Home Energy Management	Systems to shift retail load to reduce time of use energy and demand changes
Home Backup	Systems for backup power for home offices with high reliability value

## Applications of ESSs
ESS applications for wind integration support can be categorized as generation-side, grid-side and demand-side applications [11]⁠:
Generation-side Applications
Different from conventional power plants, wind farm power output cannot be controlled in a strict way as a result of stochastic nature of wind. Power intermittency, ramp rates and limiting wind power output are the main challenges coming along with wind power integration into the power systems [14]⁠. Looking from the generation-side to overall system, controllability of a wind farm can be increased with the usage of ESSs.
Time shifting: Wind power generation is a non-dispatchable source of electricity production and can only be forecasted with a limited certainty. The mismatch between wind power output with the demand pattern, e.g. high wind power generation during off-peak demand periods and vise versa, is a big challenge as the difference between peak and off-peak periods of the system net-load increases. Energy storage technologies can be used to match the wind power generation with load cycles by storing extra energy during high wind power generation and releasing it later during peak demand periods. In time shifting applications, huge amount of energy is required to be stored for long time periods, so it is important to consider storage capacity and energy to power ratio parameters of the ESSs in these applications.
Output smoothing: Wind power generation can have sudden drops and steep rises as a result of variable wind speed. System stability will be affected with the sudden power output changes which will create frequency and voltage fluctuations. Power output of a wind farm can be smoothed out with energy storage technology applications, by storing excess energy during instantaneous increase in power generation and releasing the stored energy during sudden output power drops. Ramping capability of the ESSs is the most important parameter in these applications, as the storage system must response the fast changes of wind power output.
Transmission utilization efficiency: Rich wind resources are often located in remote locations and transmission networks limitations becomes a serious problem to supply the energy demand, which is far from wind farm sites [15]⁠. With the usage of energy storage technology, efficiency of transmission utilization can be increased by reducing congestion over the network. Additionally, transmission and distribution upgrades can be deferred or in some cases avoided at all with proper usage of the ESSs.
Grid-side Applications
Increasing wind power generation reduces the stability and reliability of the grid, because of the intermittent nature of these supplies. Considering the distributed generation of wind farms over the system, net variability of the entire grid is lower compared to the integration of single wind power plant, so overall requirement of services is less than considering grid-side applications. Energy storage technologies can be used to provide ancillary services to decrease the impact of wind power generation over system stability and reliability.
Energy arbitrage/load leveling: In the electricity market, electricity prices vary during peak and off-peak hours. The variation of prices in Turkey in 2016 can be observed in Fig. 2-5 [16]⁠. Energy storage technologies can be used to reduce the gap between peak and off-peak prices, by storing low-cost energy during off-peak periods and releasing stored energy during peak periods with the higher price [17]⁠.

Fig. 2-5: Average of hourly electricity prices in Turkey [16]⁠
Frequency regulation: ESSs can be used to provide frequency regulation to the wind farms by controlling active power output of storage with frequency deviation. Primary frequency control can be applied by using droop control in local systems. Active power output of the ESSs can be controlled according to frequency change on the grid [18]⁠. For secondary frequency control, an automatic control system can arrange the power outputs to response frequency deviations.
Inertia emulation: The impact of sudden wind generation changes on frequency changes can be reduced by increasing inertia of grid. Apparent inertia of a grid can be increased with the integration of the ESSs, by controlling the active power output of the storage systems.
Oscillation damping: Sudden power changes of wind farms can cause oscillations in an interconnected system which may led to synchronization loss of some machines [19]⁠. Energy storage technologies can be used to damp the system oscillations caused by variable wind generation output and increase the stability of the power system.
Voltage control support: Voltage stability of the grid can decrease with the variable nature of wind generation output. Integration of energy storage technologies can increase reactive power support for voltage regulation by controlling converters connected to the grid [19]⁠.
Low Voltage Ride Through support: Today, low voltage ride through (LVRT) capability of wind turbine generators are determined by grid codes. During severe grid faults, wind turbines should remain connected for reactive power support and in some situations maximum reactive power needs to be delivered by wind turbines [20]⁠. For such cases, energy storage technologies can support the power need by converters and control systems.
Reserve application: For the stability and reliability of the system, emergency reserves are required as a result of forecast error of wind power output. Integration of energy storage technologies can be an option for the reserve applications.
Emergency power supply: In the situation of a fatal failure, ESSs can be used to energize the power system from a shut-down condition [21]⁠.
Transmission utilization efficiency: Integration of energy storage technologies into power systems can increase the efficiency of transmission network usage and transmission and distribution costs can be reduced by deferral of network upgrade.
Demand-side Applications
With the combination of ESSs and DSM, ancillary services can be provided for the grid using huge amount of variable loads as a virtual power plant (VPP).
## Planning of ESSs
Technical characteristics of an ESS, such as storage capacity, rating power and charging/discharging duration range can be determined by analyzing characteristics of a wind farm.
Fluctuations of wind generation output at different time scales is an important parameter for the ESS selection. While generation reserve and energy dispatch applications are related to low frequency fluctuations (minutes to hours), power system frequency control applications are related to high frequency applications (seconds to minutes) [22]⁠. High frequency fluctuations on the wind power output has an insignificant overall effect [23]⁠ and can be damped out by inertia of the turbine generator [24]⁠. As a result, it is required that energy to power ratio of the ESSs to be in the order of a few hours for wind integration support [11]⁠.
As the increasing rating capacity of wind farms is considered, large-scale energy storage technologies are required for wind integration applications. BESS, PHS and CAES technologies are suitable for the large-scale applications for their capability of storing energy for long periods at a high power rating. Among these three technologies, BESS is more suitable for the purpose, as PHS and CAES are limited by topographical constraints [25]⁠.
By taking account of the findings mentioned above and rapid development in battery technology and cost reduction, it is decided to study the BESS technology for the wind power applications. Battery types are introduced in the following with their advantages and disadvantages [26]⁠:
Lead-acid Batteries:
Advantages: Easy installation, high efficiency, low investment cost, long storage duration due to low self-discharge.
Disadvantages: Poor	performance at low and ambient temperatures, short life time, periodic maintenance requirements, low specific power, difficulties in frequent power cycling, environmentally unfriendly.
Nickel-based Batteries:
Advantages: Fast discharge cycles due to low internal resistance, long life time, low maintenance requirements, good low temperature performance, wide range of size and performance options, lowest cost per cycle [27]⁠, integration with renewable energy sources for long term storage [28]⁠.
Disadvantages: Higher cost compared to lead-acid batteries even they have lower energy efficiency and higher discharge rate [27, 28]⁠, high toxicity, full charge deficiency after series of full discharges [23]⁠, continuous maintenance requirements.
Sodium-Sulphur Batteries:
Advantages: Long life time, high power density, high energy capacity, good performance at ambient conditions [29]⁠.
Disadvantages: Thermal management, safety.
Lithium-based Batteries:
Lithium-Ion Batteries and Lithium-Polymer Batteries;
Advantages: High energy density and specific energy, fast charge and discharge capability, high efficiency, light weight, decreasing cost [27]⁠.
Disadvantages: Life time dependency on operating temperature, necessity to maintain a safe operating voltage and temperature due to high flammablity and fragility, maximum charge and discharge current limitations.
Flow Batteries:
Vanadium Redox Flow Batteries (VRB), Zinc-Bromine Flow Batteries (ZBB), Polysulphide-Bromide Flow Batteries (PSB);
Advantages: Scalability, high power, long duration, fast response and quick transition between charge and discharge modes, zero self-discharge [30]⁠.
Disadvantages: High operating cost, low energy density, thermal management need for safety.
Two mainly used battery types in BESSs are lithium-ion and lead-acid batteries and their characteristics are summarized including future expectations at Table 2.5 and Table 2.6 [10]⁠, respectively. By comparing the advantages and disadvantages of these two type of BESSs, lithium-ion batteries are chosen in this study due to high energy and power density, fast charge and discharge capability, long life time and high efficiency.
Table 2.5 Characteristics of lithium-ion batteries [10]⁠
Lithium-ion batteries
Parameters	2013	2030 (Expected)
Round-trip efficiency	83-86 %	85-92 %
Energy density	200-350 Wh/l	250-550 Wh/l
Power density	100-3500 W/l	100-5000 W/l
Cycle life	1000-5000 full cycles	3000-10000 full cycles
Calender life	5-20 years (depending on temperature and SoC)	10-30 years (depending on temperature and SoC)
Depth of discharge	Up to 100 %	Up to 100 %
Self discharge	5 % per month	1 % per month
Power installation cost (converter)	150-200 €/kW	35-65 €/kW
Energy installation cost	300-800 €/kW	150-300 €/kW
Deployment time	3-5 ms
Site requirements	None
Main applications	Frequency control / Voltage control / Peak shaving / Load leveling / Electromobility / Residential storage systems

Table 2.6 Characteristics of lead-acid batteries [10]⁠
Lead-acid batteries
Parameters	2013	2030 (Expected)
Round-trip efficiency	75-80 %	78-85 %
Energy density	50-100 Wh/l	50-130 Wh/l
Power density	10-500 W/l	10-1000 W/l
Cycle life	500-2000 full cycles	1500-5000 full cycles
Calendar life	5-15 years (depending on temperature and SoC)	10-20 years (depending on temperature and SoC)
Depth of discharge	70 %	80 %
Self discharge	0.1-0.4 % per day	0.05-0.2 % per day
Power installation cost (converter)	150-200 €/kW	35-65 €/kW
Energy installation cost	100-250 €/kW	50-80 €/kW
Deployment time	3-5 ms
Site requirements	Ventilation due to gassing
Main applications	Frequency control / Peak shaving / Load leveling / Island grids / Residential storage systems / Uninterruptible power supply

## Demand-side Management
## In a conventional power system, the balance between generation and demand is maintained by controlling the power output of limited number of power plants. However, with the increasing penetration of renewable generation to the system, dispatch of generation capacity to provide the required services to follow the load profile becoming much more challenging. As an alternative way, controlling load-side to increase flexibility of the power system attracts increasing attention. With the help of global communication infrastructure and embedded systems, loads can be dispatched according to system needs [31]⁠.
With demand-side management (DSM), flexible loads can be scheduled considering the grid needs. If individual loads can be aggregated and controlled on command according to the requirement of power systems, the result will be the same as generation dispatch. For example, turning off a large number of loads when the demand exceeds generation will have the same effect of increasing generation or vice versa.
## Classification of DSM
DSM technologies can be categorized according to timing and impact of the applications on customer process, which can be observed in Fig. 2-6 [31]⁠.

Fig. 2-6: DSM categories according to timing and impact of the appliances [31]⁠
Energy Efficiency (EE): EE applications include increasing the efficiency of appliances and improvements on the system properties. Changing a refrigerator with a more efficient one or applying thermal insulation to a building are some examples that can be considered as EE applications. In addition, behavioral changes of users to increase efficiency of energy usage can be included in these applications.
Time of Use (ToU): In ToU tariffs, electricity prices change according to power consumption at that time. Electricity prices for third quarter of 2017 in Turkey for different end-users are tabulated at Table 2.7 [32]⁠. Considering the high difference between electricity prices for different time periods of the day, customers are encouraged to arrange their power consumption to reduce the overall cost.
Table 2.7: Electric prices for different time periods in Turkey [32]⁠
End-user	Day period (06:00-17:00)	Peak period (17:00-22:00)	Night period (22:00-06:00)
Industrial	28.9365 kr/kW	44.8500 kr/kW	17.4582 kr/kW
Commercial	33.3374 kr/kW	50.2713 kr/kW	21.1035 kr/kW
Residential	33.0447 kr/kW	49.9784 kr/kW	20.8112 kr/kW

Demand Response (DR): DR is defined as controlling flexible loads to shift power consumption from peak periods to off-peak periods. By doing so, energy consumption is not decreased but only shifted through time. However, by shifting peak power consumption through time, the overall efficiency of power system is increased. Difference impacts of EE and DR applications can be observed in Fig. 2-7 [31]⁠. While EE applications affect the energy consumption permanently, DR applications only delay the energy consumption.

Fig. 2-7: Impact of EE and DR [31]⁠
Spinning Reserve (SR): Combination of large number of loads can be used for frequency regulation applications, namely primary and secondary frequency control. Primary frequency control is done by controlling active power, considering frequency changes over time. In secondary frequency control, frequency is restored with additional active power to the system. With SR applications, combination of large number of loads can be controlled like a virtual power plant with negative power output to the grid.
## Applications of DSM
DSM applications can be classified according to the time scale of the load control (from milliseconds to hours) [33]⁠:
Under a second: Frequency changes in a system can be observed and dispatchable loads can respond to these changes to maintain system security. Either loads can be shut down when a steep frequency drop occurs on the grid, or they can response to frequency changes according to frequency error, similar like droop control of conventional power plants. As wind power plants can participate to frequency control only in small amounts, demand dispatch can be a solution for the intermittent wind power output.
Seconds to minute: The ancillary services for power system regulation is provided by power plants in today’s power systems. An alternative way for serving these services to the power system is DSM. By controlling high number of loads with fast response, regulation can be provided in an efficient way.
Hours: Dispatchable loads can be controlled to match highly varying wind generation profile for a wind farm or even for a region, depending on the limits of aggregated loads. Rapid changes in wind power generation can be followed by DSM control, as the flexible loads generally have a fast response time. With the introduction of DSM into the power systems, the required fast-response generation capacity will be reduced.
## Planning of DSM
DSM takes advantage of controllable loads and support the grid considering changing needs, so in order to dispatch loads, some flexibility is needed in demand-side. Some suitable loads for DSM applications can be listed as follows [33]⁠:
- Dishwashers
- Washers and dryers
- Electric hot water heaters
- Heating, ventilation and air-conditioning (HVAC) systems
- Battery charges for consumer electronics
- Plug-in vehicles
Considering the large number of aggregated flexible loads, demand dispatch can be an important factor for the power systems applications. However, there are some constraints for the flexible loads, so important parameters must be defined for each individual load, such as minimum and maximum power limits, how much and when energy is needed and number of cycles for a given time period. The main objective of demand dispatch is to serve the grid needs by dispatching loads while considering these limitations. Suitable services for the power systems can be developed by considering power and energy limitations of flexible loads as well as their response characteristics.
HVAC systems are chosen to be controlled in this study, as they are responsible for a high percentage of energy usage in residential and commercial. End-use energy consumption for residential and commercial sectors in 2016 with the expectations in 2040 can be observed in Fig. 2-8 [34]⁠. Considering the energy consumption share overall, HVAC systems, when aggregated, can participate in matching generation and load, as well as ancillary services to support grid with suitable control methods.

Fig. 2-8: End-use energy consumption for residential and commercial sectors [34]⁠
Thermal behavior of a HVAC unit without an external control can observed in Fig. 2-9 [35]⁠. In this case, HVAC unit works as a heater only and operates according to set temperature limits with the help of the thermostat, simply turning on when room temperature is under the lower set limit and turning off when room temperature is over the upper set limit.

Fig. 2-9: Thermal behavior of a HVAC unit [35]⁠
A HVAC can be described in terms of the following properties:
Coefficient of Performance (CoP) is the HVAC efficiency measured in cooling/heating output divided by electrical power input.
Energy Efficiency Ratio (EER) is the ratio of cooling/heating capacity of HVAC to electrical power input at full-load conditions.
DSM applications can have different control methods, which usually divided into two categorizes; direct load control (DLC) and indirect load control (ILC) [36]⁠, [37]⁠. More detailed categorization according to control methods can be observed in Fig. 2-10 [38]⁠:

  Fig. 2-10: DSM categories according to control methods [38]⁠
- Direct control
In direct control method, specific commands are sent to controllable loads via an external controller, which has the information about load operation. One-way or two-way communication can be used for information exchange between direct controller and loads. For one-way communication infrastructure, commands are sent to loads via external controller and it is expected from the loads to follow the specific commands if there isn’t any violation of operation limits or failure. In case of two-way communication structure, the loads acknowledge the specific commands sent by external controller and send back the information about the applicability of the command with the status.
Different types of direct load control schemes commonly found in literature are deferred consumption, delta control, scheduled operation and direct control [39]⁠, which are explained below. Operation of direct control methods are also presented in Fig. 2-11 [38]⁠.
Deferred consumption: The consumption of the certain amount of energy is shifted through time. The command signal sent to load is a time shift (Δt).
Delta control: The consumption of the certain amount of energy is decreased or increased, which may result in change of operation duration. The command signal sent to load is a power difference (ΔP).
Scheduled operation: Schedule of power set points with time stamps is sent to load and executed locally. The command signal includes power set point and time stamp (P, t).
Direct control: Power set point is sent to load in real-time. The command signal is power set point (P).

Fig. 2-11: DSM direct load control operations: (A) Deferred consumption, (B) Delta control, (C) Scheduled operation, (D) Direct control [38]⁠
Indirect control
In case of indirect control, loads receive the command signals sent by an external controller, but not necessarily behave as commanded. Two main characteristics of indirect load control are indirectness of the relationship between control objective and observables, which can lead random unobservable behavior and non-deterministic behavior of the loads due to independent decision making of the local controllers [37]⁠. As the communication is one-way, external controller does not receive any feedback from the loads. External controller broadcasts command signals in indirect control method and any load can behave according to commands at any time or loads can follow special and dynamic objectives depending on local decision making algorithms. Indirect control methods can be divided into two categories; control with indirect functional variables indirect control via price signals [38]⁠.
Control with indirect functional variables: External controller objective is to modify the operation of the loads by sending a command signal to the load which contains a functional variable. As the state of the loads are unknown due to the lack of feedback, system behavior is non-deterministic. Functional variable signal can be generated by using the observable or estimated aggregated response and statistical models can be used to decrease the mismatch between control goal and system behavior.
Indirect control via price signals: External controller uses energy prices to generate command signals. Instantaneous and scheduled price operations are two options for this control type. In case of instantaneous price operation, the command signal consists of a single price with a time stamp which states the validation time of the price. In case of scheduled price operation, command signal consists a time series of prices and time stamps for the future.
Transactional control
Transactional control method depends on negotiations in a bid-based market in which loads are used for trading products, e.g. power, energy and flexibility. Local controllers independently determine the bidding amount and compete with each other. With the transactions, local controllers optimize the consumption by using equilibrium value determined by the market. This control method includes the price negotiation and biding strategies. Local controllers decide the bid offers and operation of the loads. Price equilibrium for all participating loads are determined by the constructed market.
Autonomous control
Local measurements are used to control the loads locally in autonomous control method. Communication infrastructure is not needed as all the decisions are taken by local controllers and due to independent local measurements, loads can response faster compared to the other control methods. This control method can be used for local power system services.
## Summary and Conclusion
This chapter started with the introduction of power system flexibility concept and two proposed methods for additional flexibility on power systems are presented; energy storage technologies and demand-side management.

# CHAPTER 3
# TRANSMISSION AND DISTRIBUTION UPGRADE DEFERRAL
## Introduction
Overloading of the existing T&D structures used in the power systems over time is a critical problem as a result of continuous growing peak demand. In order to maintain the safety of the system and the equipment, upgrade of the present structures becomes inevitable even in the situation of modest overload. The main problem of upgrading an existing T&D structure is the high investment cost, which is highly variable due to various factors, such as installation requirements and location. However, upgrade of a T&D system can be delayed in specific conditions, depending on the characteristics of the power flow. Viability of T&D upgrade deferral can be examined by checking some criteria over present systems [40]⁠:
- High T&D investment cost
- High peak-to-average demand ratio
- Modest projected overload
- Slow peak demand growth
- Uncertainty about timing and/or likelihood of block load additions
- T&D construction delays or construction resource constraints
- T&D upgrade competes with other important projects for capital
In need of an upgrade over existing structure, T&D upgrade factor is defined as the ratio of load carrying capacity to be added to present T&D structure. Common upgrade factor values range from 0.25 to 0.50 or more. An example of the T&D upgrade deferral concept is demonstrated in Fig. 3-1 [40]⁠. For this case, an existing distribution system with a rated load carrying capacity of 12 MW is expected to be overloaded next year, considering a 2% load growth rate per year. In order to avert overloading of the equipment, load carrying capacity of the distribution structure is planned to be increased with an upgrade factor of 0.33, from 12 MW to 16 MW. Taking the modest overload foresight over the structure into account, upgrade need of the present structure can be delayed for some time using proper solutions.

Fig. 3-1: Planned upgrade of a distribution system due to increasing peak demand [40]⁠
ESS and DSM can be used to deliver a portion of peak demand, as a result large T&D structure upgrades can be delayed with small capacity additions. In this chapter, constructed scenario for the T&D upgrade deferral application is explained with the analysis of obtained data integrated into the scenario. Modeling and approaches of ESS and DSM are also introduced in the next part of this chapter.
## Description of the Scenario
In this study, a scenario is constructed where a wind farm connected to a near organized industrial zone through distribution lines and overall system is connected to the transmission-side as shown in Fig. 3-2. Transmission-side capacity is occupied by power flow from/to the grid (Pgrid), which is the difference between wind power generation (Pwind) and industrial load (Poiz). Overload on the transmission-side is examined for different wind capacity growth rates over the system and the impact of ESS and DSM integration on the transmission-side structure upgrade delay is analyzed.

Fig. 3-2: Drawing of the system

Pwg

Poiz

Grid
Wind Farm

Pline

Organized Industrial Zone

loads
Wind power generation and organized industrial zone power consumption data used in this study are obtained from Monitoring and Forecasting System Development for Wind Generated Electrical Power in Turkey (RİTM, in native initials) and National Power Quality Project (MGKP, in native initials) of The Scientific and Technological Research Council of Turkey, Marmara Research Center, Energy Institute (TÜBİTAK MAM EE, in native initials). In order to use the available data, raw data are organized and processed using R, which is an open source software environment for data manipulation, calculation and graphical display.
Missing data are common problem for data analysis, and can have significant effect considering the overall study. Percentage and distribution of missing data are two important factors which needed to be taken account. Databases of aforementioned projects are examined in order to find suitable data considering percentage and distribution of missing values.
After the analysis of project databases, wind generation measurements of a wind farm in the Aegean Region of Turkey and industrial consumption measurements of an organized industrial zone in the Marmara Region of Turkey is decided to be used for this study. Both generation and consumption data are corresponding to year 2016 with 10 minute intervals. Summary of missing values in raw data used in this study is tabulated at Table 3.1. The percentage of missing data is 0.77% for wind power generation, which is an acceptable value considering the distribution of missing values. Industrial power consumption data used in this study does not contain any missing value. The missing data are interpolated by Kalman Smoothing method with the “imputeTS” library of R.
Table 3.1: Information of missing values in chosen data
	Wind power generation	Industrial power consumption
Missing data percentage	%0.77	-
Maximum number of consecutive missing data	8	-

Summary of wind power generation and industrial power consumption data after imputation of missing values are provided at Table 3.2. The high difference between maximum generation and consumption values is not favourable for this study, as the impact of wind generation is tried to be investigated over the system. In order to compensate for the difference, wind power generation data is multiplied by 4, which brings the maximum generation and consumption levels near 160 MW.
Table 3.2: Summary of wind generation data
Data	Min. (MW)	1st Qu. (MW)	Median (MW)	Mean (MW)	3rd Qu. (MW)	Max. (MW)
Wind generation	-0.24	2.78	9.62	13.2	22.13	40.83
Industrial load	-0.39	95.73	115.45	104.72	126.09	157.03

Power generation of the wind farm used in this study is plotted in Fig. 3-3. Highly variable nature of wind generation through the year can be seen in this figure. Daily wind generation of the wind farm is also plotted in Fig. 3-4, where the steep rises and sudden drops of the power output can be observed in more detail. An important factor for the feasibility of transmission-side upgrade delay is the high peak to average ratio of power flow, which is the case for power generation of the wind farm. Low percentage of high power generation levels can be observed from the histogram figure presented in Fig. 3-5.

Fig. 3-3: Power generation of the wind farm throughout the year

Fig. 3-4: Daily power generation of the wind farm

Fig. 3-5: Histogram of the wind power generation
Power consumption of the organized industrial zone used in this study is plotted in Fig. 3-6. Weekly pattern of the industrial power consumption can be observed throughout the year except the first week of July and second week of September, which are corresponding to holidays in Turkey, Ramadan and Sacrifice Feasts, respectively. Weekly power consumption of the industrial zone starting from Monday is also plotted in Fig. 3-7. As it can be observed from this figure, power consumption on weekdays has a similar pattern and on weekends, power consumption decreases significantly compared to weekdays. Power consumption levels are distributed around 120 MW for weekdays and 50 MW for weekends, which can be observed from the histogram presented in Fig. 3-8.

Fig. 3-6: Power consumption of the organized industrial zone throughout the year

Fig. 3-7: Weekly power consumption of the organized industrial zone

Fig. 3-8: Histogram of the organized industrial zone power consumption
With the integration of aforementioned wind generation and industrial consumption profiles to the system, power flow on the transmission-side and histogram of power flow levels are shown in Fig. 3-9 and Fig. 3-10, respectively. In these figures, positive power corresponds to excess power generation of wind farm which is supplied to the grid, and negative power corresponds to power demand from the grid where wind generation cannot supply the industrial load. Low percentage of peak power flow can be observed in these figures. Summary of the power flow is also tabulated at Table 3.3.

Fig. 3-9: Power flow on transmission-side as a result of chosen generation and load profiles

Fig. 3-10: Histogram of power flow on transmission-side
Table 3.3: Summary of power flow from/to grid
Data	Min. (MW)	1st Qu. (MW)	Median (MW)	Mean (MW)	3rd Qu. (MW)	Max. (MW)
Grid power flow	-149.77	-102.13	-60.46	-51.94	-8.98	142.40

Conductor types used in Turkish electricity grid for 380 kV and 154 kV transmission lines are tabulated with their characteristics at Table 3.4 and Table 3.5, respectively. In these table, current carrying capacity (A) and thermal capacity (MVA) is defined for 80 oC conductor temperature, 40 oC ambient temperature and 0.25 m/sec wind speed.
Table 3.4: 380 kV transmission line conductor types and characteristics
Type	Total conductor area (mm2)	MCM	Current carrying capacity (A)	Thermal capacity (MVA)
2B, Rail	2x517	2x954	2x755	995
2B, Cardinal	2x547	2x954	2x765	1005
3B, Cardinal	3x547	3x954	3x765	1510
3B, Pheasant	3x726	3x1272	3x925	1825

Table 3.5: 154 kV transmission line conductor types and characteristics
Type	Total conductor area (mm2)	MCM	Current carrying capacity (A)	Thermal capacity (MVA)
Hawk	281	477	496	132
Drake	468.4	795	683	182
Cardinal	547	954	765	204
2B, Cardinal	2x547	2x954	2x765	408
Pheasant	726	1272	925	247

As tabulated in Table 3.3, maximum power supplied to the grid is142.40 MW and maximum power drawn from the grid is 149.77 MW. Considering these limits, it is reasonable to choose the transmission-side of the grid as 795 MCM with 182 MVA capacity limit. For this study, different capacity increase plannings are considered for the wind farm energy in separate cases. Overload of the existing structure is avoided by analyzing each case for the present situation. It is verified from Turkish Electricity Transmission Company (TEİAŞ, in native initials) that in case of an overload over the existing transmission structure, new transmission line with the same capacity is allocated to the region, which corresponds to an upgrade factor of 1 for this study.
For this study, the impact of ESS and DSM on transmission-side upgrade deferral is investigated for the explained scenario with different cases. As mentioned in the previous chapter, battery energy storage system (BESS) is chosen for the energy storage technology on system. The BESS is integrated to the system at the point of common coupling of wind farm as shown in Fig. 3-11. For DSM application, HVAC units are determined as an suitable option because of the high percentage of end-use consumption occupied by these units. HVAC units’ power load over the system is considered in the consumption of organized industrial zone. The main purpose of this study is to use ESS and DSM concepts, in our case BESS and aggregated HVAC units, as an environment to absorb the excess power flow occurring on the transmission-side of the system. Detailed information about the cases is presented in the next chapter with the simulation results.

Fig. 3-11: Drawing of the system with BESS integration

Pwg

Poiz

Organized Industrial Zone

Grid
Wind Farm

Pline

Pbess
BESS

HVAC
units

other loads
## Modeling and Approaches
Power flow on transmission-side
Analysis of deferring the transmission-side upgrade by keeping power flow on transmission-side within the limits of transmission structures is the main purpose of this study. Power flow constraints of the transmission-side is expressed as follows:
-P_grid^max <= P_wind^k + P_bess^k - P_oiz^k <= P_grid^max	(3-1)
where:
P_grid^max	maximum transmission line loading capacity (MW)
P_wind^k	wind farm power generation at time step k (MW)
P_oiz^k	organized industrial zone power consumption at time step k (MW)
P_bess^k	BESS power output at time step k (MW)
BESS
BESS can operate in three different modes; discharging, charging and idle. In charging mode, batteries are charged with the power drawn from grid and BESS can be considered as a load. In discharging mode, the power is supplied to the grid with discharge of the batteries and BESS can be considered as a generation unit. In idle mode, batteries are neither charged nor discharged. Mode variables of BESS are tabulated at Table 3.6.
Table 3.6: Mode variables of BESS
Variable	Idle mode	Discharging mode	Charging mode
u_dsch^k	0	1	0
u_ch^k	0	0	1

where:
u_dsch^k	discharging mode indicator of the BESS at time step k
u_ch^k	charging mode indicator of the BESS at time step k
Discharging efficiency of a BESS is defined as the ratio of power supplied to grid to rate of change in stored energy in BESS. Charging efficiency of a BESS is defined as the ratio of rate of change in stored energy in BESS to power drawn from grid. Battery charging and discharging powers are limited by the physical and chemical characteristics of the BESS. Considering these information, power equations of the BESS are expressed as follows:
u_ch^k P_{bess,rt} {1} over {n_ch} <= P_bess^k <= u_dsch^k P_{bess,rt} n_dsch	(3-2)
where:
P_{ bess,rt}	rated power of the BESS (MW)
P_bess^k	power output of the BESS at time step k (MW)
u_dsch^k	discharging mode indicator of the BESS at time step k
u_ch^k	charging mode indicator of the BESS at time step k
%eta_dsch	discharging efficiency of the BESS
%eta_ch	charging efficiency of the BESS
SoC of a battery is defined as available capacity of the battery expressed as a percentage of its rated capacity. SoC is an indication of how longer a battery can continue to perform before recharging is needed [41]. Depleting or overcharging a battery is not desired, so proper limitations (i.e., 30%-100%) should be defined for SoC of the battery. Considering these information, SoC equations of the BESS are expressed as follows:
SoC^{k+1} = SoC^{k} + {( P_bess^k ((u_dsch {1} over {%eta_dsch})+(u_ch %eta_ch))) {%DELTA t} over {60}} over { S_cap }	(3-3)
S_cap = (E2P) P_{bess,rt }	(3-4)
SoC^min <= SoC^k <= SoC^max	(3-5)
where:
SoC^k	state of charge of BESS at time step k
P_bess^k	power output of the BESS at time step k (MW)
u_dsch^k	discharging mode indicator of the BESS at time step k
u_ch^k	charging mode indicator of the BESS at time step k
%eta_dsch	discharging efficiency of the BESS
%eta_ch	charging efficiency of the BESS
S_cap	storage capacity of the BESS (MWh)
E2P	energy to power ratio of the BESS (hours)
P_{bess,rt}	rated power of the BESS (MW)
SoC^min	minimum allowed state of charge of the BESS
SoC^max	maximum allowed state of charge of the BESS
HVAC
HVAC units can operate in three different modes; cooling, heating and idle. In cooling mode, HVAC units draw power from the grid to extract heat from the room. In heating mode, HVAC units draw power from the grid to release heat to the room. In idle mode, HVAC units neither cool nor heat the room. Mode variables of HVAC units are tabulated at Table 3.7.
Table 3.7: Mode variables of HVAC unit
Variable	Idle mode	Heating mode	Cooling mode
(u_ht)_i^k	0	1	0
(u_cl)_i^k	0	0	1

where:
(u_ht)_i^k	heating mode indicator of the HVACi at time step k
(u_cl)_i^k	cooling mode indicator of the HVACi at time step k
HVAC units draw power from the grid both for cooling and heating modes. Total power drawn from the grid by HVACs can be expressed as follows:
P_hvac^k = sum from i=1 to N [(P_{hvac,rt})_i ((u_ht)_i^k + (u_cl)_i^k )]	(3-6)
where:
P_hvac^k	power demand of aggregated HVAC units at time step k (MW)
(P_{hvac,rt})_i	rated power of HVACi (MW)
(u_ht)_i^k	heating mode indicator of the HVACi at time step k
(u_cl)_i^k	cooling mode indicator of the HVACi at time step k
N	number of HVAC units
CoP for cooling mode is defined as the ratio of the removed heat to electrical input power and CoP for heating mode is defined as the ratio of the delivered heat to electrical input power [42]⁠. Considering these information, thermal power output of HVAC units can be expressed as follows:
(Q_hvac)^k_i = (P_{hvac,rt})_i (((u_ht)_i^k CoP_ht)_i - (u_cl)_i^k (CoP_cl)_i)	(3-7)
where:
(Q_hvac)_i^k	equivalent thermal power output of HVACi at time step k (MW)
(P_{hvac,rt})_i	rated power of HVACi (MW)
(u_ht)_i^k	heating mode indicator of the HVACi at time step k
(u_cl)_i^k	cooling mode indicator of the HVACi at time step k
(CoP_ht)_i	heating coefficient of performance of HVACi
(CoP_cl)_i	cooling coefficient of performance of HVACi
For modeling the HVAC units, a simplified model for temperature dynamics of a space can be created using a resistance-capacitance (RC) circuit analogy [35]⁠, [43]⁠. The simplified thermal mass model can be used for energy conversion problems, considering entire building and average temperature of all building spaces, as shown in Fig. 3-12. The representation of temperature dynamics in discrete time is stated in Eq. 3-13 [43]⁠. The building temperature variation is controlled within a temperature band by HVAC units.

Fig. 3-12: Equivalent thermal parameters model of a space temperature

Ceq
Req

Tout

Qhvac
Troom

With the information given above, temperature equations of the buildings can be expressed as follows:
(T_room)_i^{k+1} = (T_room)_i^{k} + ({(T_out)_i^{k} - (T_room)_i^{k}} over {(R_eq)_i (C_eq)_i} + {(Q_hvac)_i^k} over {(C_eq)_i}) %DELTA t	(3-13)
(T_room)_i^min < (T_room)_i^k < (T_room)_i^max	(3-14)
where:
(T_room)_i^k	temperature of buildingi at time step k (Co)
(T_room)_i^min	minimum allowed temperature of buildingi (Co)
(T_room)_i^max	maximum allowed temperature of buildingi (Co)
(T_out)_i^k	temperature of ambienti at time step k (Co)
(R_eq)_i	equivalent thermal resistance of buildingi (Co/kW)
(C_eq)_i	equivalent thermal capacity of buildingi (kJ/Co)
(Q_hvac)_i^k	equivalent thermal power output of HVACi at time step k (kW)
For this thesis, ambient temperature data is collected from U.S. Climate Reference Network (USCRN) [44]⁠, as there is no accessible weather datasets of Turkey for sub hourly periods. In order to simulate suitable ambient temperature conditions for the operations of HVAC units, USCRN monthly temperature data for 2016 are compared with the monthly temperature data collected from Turkish State Meteorological Service (MGM, in native initials) [45]⁠ for an area in Turkish Aegean Region between 1929-2016. Monthly data of average temperature with minimum and maximum temperature averages taken from USCRN and MGM are tabulated at Table 3.8 and Table 3.9, and collected data are plotted in Fig. 3-13 and Fig. 3-14, respectively.
Table 3.8: Summary of monthly temperature data taken from USCRN [44]⁠
	Average Temperature	Average Low Temperature	Average High Temperature
January	6.4	3.2	10.2
February	10.5	4.7	17.9
March	10.9	5.7	16.8
April	14.9	8.1	22.5
May	17.7	10.8	25.5
June	23.5	15.2	32.4
July	26.2	16.6	36.1
August	26.2	16.6	37.1
September	22.6	13.8	32.6
October	14.1	9.3	19.9
November	9.6	5.7	15.4
December	5.2	0.6	11.2

Fig. 3-13: Temperature of the chosen area from USCRN for one year period
Table 3.9: Summary of monthly temperature data taken from TSMS [45]⁠
	Average Temperature	Average Low Temperature	Average High Temperature
January	6.7	3.0	10.8
February	7.9	3.6	12.6
March	10.6	5.2	16.1
April	15.2	8.8	21.3
May	20.4	13.2	27
June	25.3	17.4	32.1
July	28.0	20.3	34.9
August	27.6	20.2	34.9
September	23.3	16.0	30.6
October	17.8	11.6	24.3
November	12.2	7.4	17.5
December	8.2	4.5	12.5

Fig. 3-14: Temperature of the chosen area from TSMS for one year period
## Conclusion

# CHAPTER 4
# SIMULATIONS AND RESULTS
## Introduction

## Control Algorithms
## HVAC Control
HVAC units can operate in cooling or heating mode, depending on the ambient temperature. As the ambient temperature difference between day and night can be large as shown in Fig. 4-1, days are divided into two periods for assigning the operation mode of HVAC units; namely day period and night period. By taking the sunrise and sundown times into account, day period is defined as the time between 07:00 and 19:00 and night period is defined as the time between 19:00 and 07:00. Ambient temperature values are assumed to be forecasted without any error and operation mode of HVAC units throughout the year is determined by comparing the average of ambient temperature values for each period with desired room temperature, which is determined as 22 oC for this study. Ambient temperature throughout the year and corresponding cooling mode and heating mode of HVAC units are presented in Fig. 4-2, Fig. 4-3 and Fig. 4-4, respectively.

Fig. 4-1: Daily variation of ambient temperature

Fig. 4-2: Ambient temperature throughout the year

Fig. 4-3: Cooling mode set of HVAC units throughout the year

Fig. 4-4: Heating mode set of HVAC units throughout the year
In this study, HVAC units are controlled by direct control method with a central controller. Two-way communication is used between the external controller and HVAC units. Flowchart of HVAC units’ control algorithm is presented in Fig. 4-5.

Fig. 4-5: Flowchart of HVAC units' control algorithm

# CHAPTER 5
# CONCLUSION

REFERENCES

[1]	U.S. Energy Information Administration, “International Energy Outlook 2016,” 2016.
[2]	“WIND IN NUMBERS | GWEC.” [Online]. Available: http://www.gwec.net/global-figures/wind-in-numbers/. [Accessed: 11-May-2017].
[3]	GWEC, “Global wind report 2016,” 2017.
[4]	TWEA, “Turkish wind energy statistics report,” 2017.
[5]	“Enercon.” [Online]. Available: http://www.enercon.de/en/products/ep-2/e-70/. [Accessed: 28-Aug-2017].
[6]	Y. Sun, Z. Zhang, G. Li, and J. Lin, “Review on frequency control of power systems with wind power penetration,” in Power System Technology, 2010, pp. 1–8.
[7]	H. T. Le, S. Santoso, and T. Q. Nguyen, “Augmenting wind power penetration and grid voltage stability limits using ESS: Application design, sizing, and a case study,” IEEE Trans. Power Syst., vol. 27, no. 1, pp. 161–171, 2012.
[8]	“Commercialisation of energy storage in europe,” 2015.
[9]	J. Cochran et al., “Flexibility in 21st Century Power Systems,” 2014.
[10]	G. Fuchs, B. Lunz, M. Leuthold, and D. U. Sauer, “Technology overview on electricity storage,” 2012.
[11]	H. Zhao, Q. Wu, S. Hu, H. Xu, and C. N. Rasmussen, “Review of energy storage system for wind power integration support,” Appl. Energy, vol. 137, pp. 545–553, 2015.
[12]	IEC, “Electrical energy storage - white paper,” 2011.
[13]	“Electric Energy Storage Technology Options: A White Paper Primer on Applications, Costs, and Benefits,” 2010.
[14]	S. Teleke, M. E. Baran, S. Member, S. Bhattacharya, and A. Q. Huang, “Optimal Control of Battery Energy Storage for Wind Farm Dispatching,” IEEE Trans. Energy Convers., vol. 25, no. 3, pp. 787–794, 2010.
[15]	EERE, “Advantages and challenges of wind energy.” [Online]. Available: https://energy.gov/eere/wind/advantages-and-challenges-wind-energy. [Accessed: 08-Jun-2017].
[16]	EPİAŞ, “Elektrik piyasası özet bilgiler raporu,” 2017.
[17]	G. Celli, S. Mocci, F. Pilo, and M. Loddo, “Optimal integration of energy storage in distribution networks,” in 2009 IEEE Bucharest PowerTech: Innovative Ideas Toward the Electrical Grid of the Future, 2009, pp. 1–7.
[18]	J. Morren, S. Member, S. W. H. De Haan, W. L. Kling, and J. A. Ferreira, “Wind Turbines Emulating Inertia and Supporting Primary Frequency Control,” vol. 21, no. 1, pp. 2005–2006, 2006.
[19]	M. Swierczynski, R. Teodorescu, C. N. Rasmussen, P. Rodriguez, and H. Vikelgaard, “Overview of the energy storage systems for wind power integration enhancement,” in 2010 IEEE International Symposium on Industrial Electronics, 2010, pp. 3749–3756.
[20]	D. D. Banham-Hall, G. A. Taylor, C. A. Smith, and M. R. Irving, “Flow batteries for enhancing wind power integration,” IEEE Trans. Power Syst., vol. 27, no. 3, pp. 1690–1697, 2012.
[21]	EPRI, “EPRI-DOE handbook supplement of energy storage for grid connected wind generation applications,” 2004.
[22]	T. Zhang, Z. J. Bao, G. Chen, Q. Yang, and W. J. Yan, “Control strategy for a hybrid energy storage system to mitigate wind power fluctuations,” in 2013 6th International Conference on Advanced Computational Intelligence, ICACI 2013 - Proceedings, 2013, pp. 27–32.
[23]	H. Chen, T. N. Cong, W. Yang, C. Tan, Y. Li, and Y. Ding, “Progress in electrical energy storage system: A critical review,” Prog. Nat. Sci., vol. 19, no. 3, pp. 291–312, 2009.
[24]	W. Li, G. Joós, and C. Abbey, “Wind power impact on system frequency deviation and an ESS based power filtering algorithm solution,” in 2006 IEEE PES Power Systems Conference and Exposition, PSCE 2006 - Proceedings, 2006, pp. 2077–2084.
[25]	D. L. Yao, S. S. Choi, K. J. Tseng, and T. T. Lie, “Determination of short-term power dispatch schedule for a wind farm incorporated with dual-battery energy storage scheme,” IEEE Trans. Sustain. Energy, vol. 3, no. 1, pp. 74–84, 2012.
[26]	A. H. Fathima and K. Palanisamy, “Battery Energy Storage Applications in Wind Integrated Systems – A Review,” in International Conference on Smart Electric Grid (ISEG), 2014, pp. 1–8.
[27]	F. Díaz-González, A. Sumper, O. Gomis-Bellmunt, and R. Villafáfila-Robles, “A review of energy storage technologies for wind power applications,” Renew. Sustain. Energy Rev., vol. 16, no. 4, pp. 2154–2171, 2012.
[28]	I. Hadjipaschalis, A. Poullikkas, and V. Efthimiou, “Overview of current and future energy storage technologies for electric power applications,” Renew. Sustain. Energy Rev., vol. 13, no. 6–7, pp. 1513–1522, 2009.
[29]	S. Koohi-Kamali, V. V. Tyagi, N. A. Rahim, N. L. Panwar, and H. Mokhlis, “Emergence of energy storage technologies as the solution for reliable operation of smart power systems: A review,” Renew. Sustain. Energy Rev., vol. 25, pp. 135–165, 2013.
[30]	K. C. Divya and J. Østergaard, “Battery energy storage technology for power systems-An overview,” Electr. Power Syst. Res., vol. 79, no. 4, pp. 511–520, 2009.
[31]	P. Palensky and D. Dietrich, “Demand side management: Demand response, intelligent energy systems, and smart loads,” IEEE Trans. Ind. Informatics, vol. 7, no. 3, pp. 381–388, 2011.
[32]	“Enerji Piyasası Düzenleme Kurumu (EPDK).” [Online]. Available: http://www.epdk.org.tr/TR/Dokumanlar/TDB/Elektrik. [Accessed: 02-Aug-2017].
[33]	A. Brooks, E. Lu, D. Reicher, C. Spirakis, and B. Weihl, “Demand dispatch,” IEEE Power and Energy Magazine, vol. 8, no. 3, pp. 20–29, 2010.
[34]	EIA, “Annual energy outlook 2017,” 2017.
[35]	N. Lu, “An evaluation of the HVAC load potential for providing load balancing service,” IEEE Trans. Smart Grid, vol. 3, no. 3, pp. 1263–1270, 2012.
[36]	M. Ifland, N. Exner, and D. Westermann, “Appliance of direct and indirect demand side management,” in IEEE EnergyTech, 2011, pp. 1–6.
[37]	K. Heussen, S. You, B. Biegel, L. H. Hansen, and K. B. Andersen, “Indirect Control for Demand Side Management – A Conceptual Introduction,” 2012.
[38]	A. M. Kosek, G. T. Costanzo, H. W. Bindner, and O. Gehrke, “An overview of demand side management control schemes for buildings in smart grids,” in IEEE International Conference on Smart Energy Grid Engineering (SEGE), 2013, pp. 1–9.
[39]	O. Gehrke and F. Isleifsson, “An aggregation friendly information model for demand side resources,” in IEEE Conference on Local Computer Network (LCN), 2010, pp. 1019–1023.
[40]	J. Eyer, “Electric utility transmission and distribution upgrade deferral benefits from modular electricity storage,” 2009.
[41]	“Battery State of Charge Determination.” [Online]. Available: http://www.mpoweruk.com/soc.htm. [Accessed: 12-May-2017].
[42]	“Cooling Load - Convert kW/ton to COP or EER.” [Online]. Available: http://www.engineeringtoolbox.com/cop-eer-d_409.html. [Accessed: 23-Jul-2017].
[43]	Y. Ma, A. Kelman, A. Daly, and F. Borrelli, “Predictive Control for Energy Efficient Buildings with Thermal Storage: Modeling, Stimulation, and Experiments,” IEEE Control Syst., vol. 32, no. 1, pp. 44–64, 2012.
[44]	H. J. Diamond et al., “U.S. climate reference network after one decade of operations status and assessment,” Bull. Am. Meteorol. Soc., vol. 94, no. 4, pp. 485–498, 2013.
[45]	“Meteoroloji Genel Müdürlüğü (MGM).” [Online]. Available: https://mgm.gov.tr/veridegerlendirme/il-ve-ilceler-istatistik.aspx. [Accessed: 31-Jul-2017].