CHAPTER 1
1. GENERAL BACKGROUND AND LITERATURE REVIEW
  1. Motivation of the Thesis

  1. Aims of the Research

  1. Outline of the Thesis
This thesis is divided into five chapters and organized as follows:
In chapter 2, general background on flexibility in power systems and ESSs are explained. Literature review on related issues are also provided in this chapter.
In chapter 3, modeling of proposed control algorithm is provided.
In chapter 4, case studies and analysis results are provided and explained.
In chapter 5, the thesis is concluded and possible future works on that subject are discussed.
CHAPTER 2
FLEXIBILITY IN POWER SYSTEMS
For power systems, flexibility can be defined as the ability of the system to maintain the balance between generation and consumption over changing conditions. Variability and uncertainty are important issues for power systems, and to cover the deviations from equilibrium and unexpected situations, enough energy resources are needed. However, the capacity of resources for the flexibility of given power system must be analyzed carefully as providing flexibility is rather expensive.
With the increasing penetration of renewable generations such as wind and solar energies to power systems, energy balance problem becomes harder to achieve, as a consequence of unpredictable and varying nature of renewable sources. Energy storage and demand side management schemes are gaining popularity over the years, which can be combined with renewable energy sources to increase flexibility of power systems.
  1. Impact of Wind on Power Systems
With the increasing environmental impacts of electricity production, renewable generation, such as wind and solar energies, has been penetrating to the power systems over the years. Today, 3.7% of global electricity is supplied by wind power and this percentage is expected to increase for the next years [1]⁠. Total installed wind power capacity has reached to approximately 487,000 MW at the end of 2016 and is expected to reach around 790,000 MW in 2020 [2]⁠. Installed wind capacity over years can be observed in Figure X [3]⁠.
Figure X Historical development of global installed wind capacity
With the increasing penetration of wind energy to power systems, security and reliability of power systems are negatively affected, as a consequence of unpredictable and varying nature of wind. Power output of wind turbine is highly dependent on wind speed and can be expressed as follows:
P = {1} over {2} {ρ} rsub {air} {C} rsub {p} left (λ , β right ) π {r} ^ {2} {v} ^ {3} (X)
where:
Cp(λ,β)	power coefficient, a function of tip speed ratio λ and pitch angle β
r	blade length
v	wind velocity
As it can be observed from Equation X, even small variations of wind speed can cause large power fluctuations. In Figure X, fluctuations of power output for a wind farm in Turkey can be observed. The figure shows that the power output can have steep rises and sudden drops. Power level frequencies of the wind farm can also be seen in Figure X.
Figure X Generation of a wind farm annually

Figure X Generation levels of a wind farm annually
With the increasing penetration of wind power into power systems, complexity of operation and planning of the systems increases. To cope with unpredictable and variable nature of wind, more power system flexibility is needed for high wind power penetration. To maintain reliability and security of the systems, additional reserves are needed. Energy storage technologies and demand side management schemes can be used for this purpose.
  1. Energy Storage Systems (ESSs)
In a power system, energy demand must be supplied instantaneously to preserve stability and quality of the system. Stability and quality of a power system decreases as an imbalance between supply and demand occurs. Scheduling of power systems with varying net load profile decreases the overall efficiency because of the deviations from optimal generation spot.
With the increasing penetration of renewable energy to power systems, security and reliability issues must be handled carefully, because of unpredictable and inconsistent nature of renewable energy sources. To cope with this problem, ESSs can be used to smooth out variable power generation of renewable energy systems, which makes renewable sources more reliable.
With the help of ESSs, electrical energy can be stored when generation exceeds consumption and stored energy can be used later for compensating generation shortage when needed. By doing this, generation can be maintained at a constant level, which increases the overall efficiency of the system. These systems can also be used for balancing short-term power fluctuations.
The form of stored energy is a widely-used way for the categorization of ESSs [4]⁠:
- Mechanical storage systems
  - Pumped hydro storage (PHS)
  - Compressed air energy storage (CAES)
  - Flywheel energy storage (FES)
- Electrochemical storage systems
  - Secondary batteries
  - Flow batteries
- Chemical energy storage
  - Hydrogen
  - Synthetic natural gas (SNG)
- Electrical storage system
  - Double-layer capacitor (DLC)
  - Superconducting magnetic energy storage (SMES)
- Thermal storage systems

Among all ESS forms, mechanical energy storage systems are the most widely used ones. With 162 GW capacity, PHS systems are by far the most used storage technology all around the world [5]⁠.
General properties of ESSs can be described as follows [6]⁠:
- Capacity: maximum energy storage limit of the system
- Power: charge/discharge power limit of the system
- Efficiency: ratio of the energy provided by discharging the system to the energy needed to charge the system
- Storage period: duration of stored energy without discharging
- Charge/discharge time: time to charge/discharge the system
- Cost: the capital and operation costs of the system
While choosing the suitable ESSs for a given system, these given properties must be carefully analyzed. Capacity and power are two important parameters for these systems. Capacity rate can be determined by control and energy management procedures while power rate can be determined by the difference between supply and demand.
Common applications of ESSs and their requirements for these applications are summarized at Table X [7]⁠. Different usage of ESSs for RES applications are also listed in Table X [8]⁠.
Table X
Table X

Battery Energy Storage Systems (BESSs)
BESSs can be used for compensation of intermittent power output of wind farms. By charging and dicharging BESSs, excess power above predefined threshold levels can be stored and delivered lately. By combining BESSs with wind power generation, throughput of the existing grid infrastructure can be improved. However, it is important to adapt control strategies for optimal use of BESSs, as large-scale utilization of BESSs is not a cost effective choice [9].
BESSs are connected to the system at the point of common coupling and power converters are used for charging/discharging operations of BESSs which is shown in Figure X.
Figure X

Thermal Energy Storage (TES)
Introduction
TES technology is used for storing thermal energy by heating or cooling a storage medium, to be used for heating and cooling needs later. Buildings and industrial processes are the main sectors where TES units are used. With the utilization of TES units, electricity consumption of the buildings does not have to be instantenously with the heating or cooling demand, as heating or cooling demand can be supplied with stored energy, which can be applied to shift electricity consumption. With the effective control of TES units, electric load profile for building’s thermal needs can be rearranged without affecting total energy consumption or temperature comfort for the buildings.
Thermal energy can be stored in three ways, in the form of sensible heat, latent heat or thermo-chemical energy. In the form of sensible heat storage, thermal energy is stored by heating or cooling a liquid or solid storage medium. In the form of latent heat storage, phase change materials (PCMs) are used for storing thermal energy. Thermo-chemical storage (TCS) is based on chemical reactions to store and release thermal energy.
Sensible heat storage is based on the specific heat of a storage medium which limits the storage capacity of these systems. PCMs use latent heat of the phase change and stored energy can be much more higher compared to sensible heat storage. In TCS, thermo-chemical reactions are used to store thermal energy for heating and cooling applications and in these systems storage capacity can be much higher.
Performance of TES units depends on system application and needs. PCM and TCS systems are more expensive compared to sensible heat storage and are suitable for applications where high number of storage cycles are needed.
Chilled water is generated with chillers and cooling towers. Chillers are used for removing the heat from chilled water loop and cooling towers are used for rejecting the heat from chiller cycle to ambient environment.
Storage element is used for shifting cooling thermal energy load. Load shifting logic depends on several factors such as renewable energy penetration, ambient temperature, temperature comfort level.

# CHAPTER 3
1. MODELING AND APPROACHES
  1. BESS Model
    1. Operating Mode
BESS can operate in three modes; charging, discharging and idle. In charging mode, batteries are charged with the power drawn from grid and BESS can be considered as a load. In discharging mode, batteries are discharged and deliver power to the grid and BESS can be considered as a generation unit. In idle mode, batteries are neither charged nor discharged.
    1. Energy Constraints
Charging efficiency of a BESS is defined as the ratio of rate of change in stored energy in BESS to power drawn from grid in charging mode.
Discharging efficiency of a BESS is defined as the ratio of power supplied to grid to rate of change in stored energy in BESS in discharging mode.
SoC of a battery is defined as available capacity of the battery expressed as a percentage of its rated capacity. SOC is an indication of how longer a battery can continue to perform before recharging is needed [10]. Depleting or overcharging a battery is not desired, so proper limitations (i.e., 30%-100%) should be defined for SoC of the battery.
Considering above definitions and limitations, energy equations for BESS model are expressed as;
E^BESS_{t}=E^BESS_{t-1} + (P^{BESS,ch}_t %eta_{BESS,ch} - P^{BESS,dch}_t %eta_{BESS,dch}) %DELTA t (X)
SoC^BESS_{t} = E^BESS_{t} / E^BESS_{max} (X)
SoC^BESS_min < SoC^BESS_{t} < SoC^BESS_max (X)
    1. Power Constraints
Battery charging and discharging speeds are limited by the physical and chemical characteristics of the BESS. With increasing depth of discharge (DoD), cycle life of a battery decreases and deep discharge can cause permanent damage over battery cells. To protect the battery from a permanent damage and increase the battery cycle life, proper limitation should be set for maximum discharge rating of the battery [11].
Considering above limitations, power equations for BESS model are expressed as;
0 < P^{BESS,ch}_t < P^{BESS,ch}_max (X)
0 < P^{BESS,dch}_t < P^{BESS,dch}_max (X)
  1. TESS Model
Main components of centralized chilled water generation system with a TESS can be observed in Figure X.
In the system, chillers and cooling towers generate chilled water. In refrigeration cycle, heat is removed from return chilled water by chillers and cooling towers reject heat from the chiller cycle to the environment.
For the storing element, a water tank which can store chilled water is considered. The water tank is considered as a stratified system because the warmer water at the top and cooler water at the bottom are mixed negligibly [12].

cooling
towers
Buildings
chillers

thermal
storage

Figure X
    1. Operating Mode
TESS can operate in three modes; charging, discharging and idle. In charging mode, when the output cooling power of chillers is greater than the cooling power need by buildings, the excess cooling power is stored in TESS. In discharging mode, when the output cooling power of chillers is less than the cooling power need by buildings, TESS compensates for the cooling power difference. In idle mode, TESS is neither charged or discharged.
    1. Energy Constraints
Charging efficiency of a TESS is defined as the ratio of rate of change in stored energy in TESS to power drawn from chiller in charging mode. Energy of TESS decreases with charging as the chilled water mass is increases.
Discharging efficiency of a TESS is defined as the ratio of rate of change in stored energy in TESS to power supplied to buildings in discharging mode. Energy of TESS increases with discharging as the chilled water mass is decreases.
Energy limitations of the TESS is defined as internal energy of the water, which is set with the cool and warm water mass limitations.
Considering above definitions and limitations, energy equations for BESS model are expressed as;
E^TESS_{t}=E^TESS_{t-1} - (P^{TESS,ch}_t %eta_{TESS,ch} - P^{TESS,dch}_t %eta_{TESS,dch}) %DELTA t (X)
E^TESS_min < E^TESS_{t} < E^TESS_max (X)
    1. Power Constraints
Efficiency of a chiller is defined as the ratio of output cooling power to input electrical power.
Charging and discharging speeds of TESS are limited by the chiller and pump characteristics of the system.
Considering above limitations, power equations for TESS model are expressed as;
P^{chiller}_o = P^{chiller}_i %eta_{chiller} (X)
0 < P^{TESS,ch}_t < P^{TESS,ch}_max (X)
0 < P^{TESS,dch}_t < P^{TESS,dch}_max (X)
    1. Temperature Constraints
A simplified model for temperature dynamics of a space can be created using a resistance-capacitance (RC) circuit analogy [12],
C dot T = u + P_{d} + ( T_{o} - T ) over R (X)
where
T	inside temperature
Pd	external disturbance load
To	outside temperature
u	heating and cooling power input
The simplified thermal mass model (X) can be used for energy conversion problems, considering entire building and average temperature of all building spaces.
For discrete time, equation (X) can be represented with a sampling time of Δt,
T(k+1) = A T(k) + B u(k) + d(k) (X)
where:
A = 1- {Δt} over {R C} , B = {Δt} over {C} , d = {P_{d} Δt} over {C} + {T_{o} Δt} over {R C}
For the simplification of building model, Pd is ignored and equation (X) becomes,
T_{change} = {Δt} (u over C + {T_{o} - T} over RC) (X)
CHAPTER 4
SIMULATIONS AND RESULTS
In this thesis, power system computer-aided design (PSCAD)/ electromagnetic transients including dc (EMTDC) is used for the simulations.
Actual power generation and power consumption datas from different wind farms and organized industrial zones are used in simulations. R programming language is used for data analysis and missing data interpretation and processed datas are imported to PSCAD/EMTDC to be used in simulations.
Figure (X)

Figure (X)

Figure (X)

Figure (X)
50 MW 500 MWh BESS
CHAPTER 5
CONCLUSIONS AND FUTURE WORK

[1]	“WIND IN NUMBERS | GWEC.” [Online]. Available: http://www.gwec.net/global-figures/wind-in-numbers/. [Accessed: 11-May-2017].
[2]	“Cumulative-Market-Forecast-by-Region-2016-2020-1.jpg (2091×1123).” [Online]. Available: http://www.gwec.net/wp-content/uploads/2016/04/Cumulative-Market-Forecast-by-Region-2016-2020-1.jpg. [Accessed: 11-May-2017].
[3]	“Global-Cumulative-Installed-Wind-Capacity-2001-2016.jpg (2092×739).” [Online]. Available: http://www.gwec.net/wp-content/uploads/2012/06/Global-Cumulative-Installed-Wind-Capacity-2001-2016.jpg. [Accessed: 23-May-2017].
[4]	K. Han and T. Carson, “Executive summary,” Management, vol. II, pp. 10–16, 2008.
[5]	“DOE Global Energy Storage Database.” [Online]. Available: http://www.energystorageexchange.org/projects/data_visualization. [Accessed: 23-May-2017].
[6]	D. Zhou et al., “Technology Roadmap,” SpringerReference, vol. 92, no. January, p. 24, 2013.
[7]	B. Zakeri and S. Syri, “Electrical energy storage systems: A comparative life cycle cost analysis,” Renew. Sustain. Energy Rev., vol. 42, pp. 569–596, 2015.
[8]	EPRI, “Electric Energy Storage Technology Options: A White Paper Primer on Applications, Costs and Benefits,” Epri, pp. 1–170, 2010.
[9]	S. Teleke, M. E. Baran, S. Member, S. Bhattacharya, and A. Q. Huang, “Optimal Control of Battery Energy Storage for Wind Farm Dispatching,” IEEE Trans. Energy Convers., vol. 25, no. 3, pp. 787–794, 2010.
[10]	“Battery State of Charge Determination.” [Online]. Available: http://www.mpoweruk.com/soc.htm. [Accessed: 12-May-2017].
[11]	“Battery Life and How To Improve It.” [Online]. Available: http://www.mpoweruk.com/life.htm. [Accessed: 12-May-2017].
[12]	Y. Ma, A. Kelman, A. Daly, and F. Borrelli, “Predictive Control for Energy Efficient Buildings with Thermal Storage: Modeling, Stimulation, and Experiments,” IEEE Control Syst., vol. 32, no. 1, pp. 44–64, 2012.